## XLog
File | Version | User | Date | Change Log
RCU mem map.BW-SA1-4BR-TypeA.xlsx | 09 | Mahesh Uddama | 13/7/2023 | - Compiled using XC Ver-0.9.0
Historical Data
RCU mem map.BW-SA1-4BR-TypeA | 08 | Mahesh Uddama | 1/8/2022 | - safe update tag min max to 19-28
| 07 | Mahesh Uddama | 22/5/2022 | - remove tag min max sending from logic tag flash settings. allowing server to send all times
| 06 | Mahesh Uddama | 26/12/2020 | - implemented cause and interrupt model
| 05 | Mahesh Uddama | 11/8/2020 | - implement delayed wc, to avoid bounce back effect
| 04 | Mahesh Uddama | 19/3/2020 | - guest staff has same role - lock pair loss, take door contact as user presence management - tag brightness settings - FCU actuator ration 1 degree
Historical Data

## Device1
| ;Devices.hex | [9 empty] | Event map |  |  | Dir: | C:\tini\ModularHotel\ABSlink\RCUmanager\bin\Release
| ;Enum | Type | Id | COM | Pt Event map |  |  |  | lo hi |  | 16bit pt to program |  |  | 0000=none |  |  |  | Enum/Priority
| ;/Priority |  |  |  | lo hi |  | EnumHex | Enum | Progran |  | Start with RCU event |  |  | 8000=activate standard management |  |  |  | Enum is used in multi devices to manage variable offseting
1 | 01 | 01 | 0A | 01 | 21 00 | ;IDPG1 | 00 | 0 | 00 00; | RCU | Startup |  |  | 4000=only on guest presence
2 | 01 | 10 | 14 | 03 | 01 01 | ;RCU2 Slave 1 | 01 | 1 | 00 00; |  | Watchdog |  |  | bit 15 permit to flag both (standard+program)
3 | 11 | 10 | 15 | 03 | 12 01 | ;RCU3 Slave 2 | 02 | 2 | 00 00; |  | Battery | start |  | bit 14 only guest action
4 | 21 | 10 | 16 | 03 | 23 01 | ;RCU4 Slave 3 | 03 | 3 | 00 00; |  | Battery | end
5 | 01 | 03 | 1E | 01 | 37 00 | ;TAG1 | 04 | 4 | 00 00; |  | Battery | low |  | Types
6 | 11 | 03 | 1F | 01 | 5B 00 | ;TAG2 | 05 | 5 | A4 00; |  | Input | 1 on | door_contact_close | 1 | IDPG
7 | 21 | 03 | 20 | 01 | 6D 00 | ;TAG3 | 06 | 6 | 9D 00; |  | Input | 1 off | door_open | 2 | TIG
8 | 31 | 03 | 21 | 01 | 7F 00 | ;TAG4 | 07 | 7 | 5A 01; |  | Input | 2 on | window_close | 3 | TAG
9 | 41 | 03 | 22 | 01 | 91 00 | ;TAG5 | 08 | 8 | 3D 01; |  | Input | 2 off | window_open | 4 | IOEXP
10 | 51 | 03 | 23 | 01 | A3 00 | ;TAG6 | 09 | 9 | E1 04; |  | Input | 3 on | pir1_close | 5 | IODEXP
11 | 01 | 04 | 64 | 02 | 49 00 | ;IOEXP1 F06A | 0A | 10 | 12 05; |  | Input | 3 off | pir1_open | 6 | GSW |  | IOEXP with polling on Input
12 | 11 | 04 | 65 | 02 | 49 00 | ;IOEXP2 B02A | 0B | 11 | E7 04; |  | Input | 4 on | pir2_close | 7 | IOEXPIN
13 | 01 | 0C | 80 | 02 | EB 00 | ;Temp-hub1 | 0C | 12 | 17 05; |  | Input | 4 off | pir2_open | 8 | BSP RF
14 | 11 | 0C | 81 | 02 | EC 00 | ;Temp-hub2 | 0D | 13 | ED 04; |  | Input | 5 on | pir3_close | 9 | BSP wired
15 | 21 | 0C | 82 | 02 | ED 00 | ;Temp-hub3 | 0E | 14 | 1C 05; |  | Input | 5 off | pir3_open | 128 | General Modbus
16 | 31 | 0C | 83 | 02 | EE 00 | ;Temp-hub4 | 0F | 15 | F3 04; |  | Input | 6 on | pir4_close | 129 | General IP |  | Id+Com=Port Pt=last 2 IP addr
17 | 41 | 0C | 84 | 02 | EF 00 | ;Temp-hub5 | 10 | 16 | 21 05; |  | Input | 6 off | pir4_open
18 | 51 | 0C | 85 | 02 | F0 00 | ;Temp-hub6 | 11 | 17 | F9 04; |  | Input | 7 on | pir5_close | Id | FF | Server
19 | 01 | 0B | 70 | 04 | F2 00 | ;KABA/Vingcard | 12 | 18 | 26 05; |  | Input | 7 off | pir5_open |  | FE | Calling device
20 | 01 | 06 | 28 | 01 | B5 00 | ;GSW02 A | 13 | 19 | FF 04; |  | Input | 8 on | pir6_close
21 | 11 | 06 | 2A | 01 | D0 00 | ;GSW01 | 14 | 20 | 2B 05; |  | Input | 8 off | pir6_open
[7 empty] | 15 | 21 | 2A 80; |  | Thermo | on | thermo_cycle
[7 empty] | 16 | 22 | 00 00; |  | Evt grp write (reg)
[7 empty] | 17 | 23 | 00 00; |  | Evt grp write (reg)
[7 empty] | 18 | 24 | 7E 02; |  | Input | 9-24 on | top_inputs_on
[7 empty] | 19 | 25 | 87 02; |  | Input | 9-24 off | top_inputs_off
[7 empty] | 1A | 26 | 00 00; |  | SOS | off
[7 empty] | 1B | 27 | 00 00; |  | Laundry | on
[7 empty] | 1C | 28 | 00 00; |  | Laundry | off
[7 empty] | 1D | 29 | 00 00; |  | Call | on
[7 empty] | 1E | 30 | 00 00; |  | Call | off
[7 empty] | 1F | 31 | 00 00; |  | Card Ok
[7 empty] | 20 | 32 | 00 00; |  | Card Nok
[7 empty] | 21 | 33 | 2C 00; | IDPG1 | Offline |  | dev_offline
[7 empty] | 22 | 34 | 3D 80; |  | Bell |  | bell_idpg
[7 empty] | 23 | 35 | 00 00; |  | Bell with DnD
[7 empty] | 24 | 36 | 00 00; |  | Card Ok
[7 empty] | 25 | 37 | 00 00; |  | Card Nok
[7 empty] | 26 | 38 | 00 00; |  | Input 1 on
[7 empty] | 27 | 39 | 00 00; |  | Input 1 off
[7 empty] | 28 | 40 | 00 00; |  | Input 2 on
[7 empty] | 29 | 41 | 00 00; |  | Input 2 off
[7 empty] | 2A | 42 | 00 00; | TIG1 | OffLine
[7 empty] | 2B | 43 | 00 00; |  | DND | down
[7 empty] | 2C | 44 | 00 00; |  | DND | up
[7 empty] | 2D | 45 | 00 00; |  | Master | down
[7 empty] | 2E | 46 | 00 00; |  | Master | up
[7 empty] | 2F | 47 | 00 00; |  | MUR | down
[7 empty] | 30 | 48 | 00 00; |  | MUR | up
[7 empty] | 31 | 49 | 00 00; |  | Card Pocket Insert
[7 empty] | 32 | 50 | 00 00; |  | Card pocket Extract
[7 empty] | 33 | 51 | 00 00; |  | Input 1 on
[7 empty] | 34 | 52 | 00 00; |  | Input 1 off
[7 empty] | 35 | 53 | 00 00; |  | Input 2 on
[7 empty] | 36 | 54 | 00 00; |  | Input 2 off
[7 empty] | 37 | 55 | 2C 00; | TAG1 | OffLine |  | dev_offline
[7 empty] | 38 | 56 | 00 00; |  | C/F
[7 empty] | 39 | 57 | 00 00;
[7 empty] | 3A | 58 | 00 00; |  | out temp
[7 empty] | 3B | 59 | 2A 41; |  | Btn - |  | tag1_readsetpoint
[7 empty] | 3C | 60 | 2A 41; |  | Btn + |  | tag1_readsetpoint
[7 empty] | 3D | 61 | FF 40; |  | Fan1 |  | tag1_fan1
[7 empty] | 3E | 62 | 05 41; |  | Fan2 |  | tag1_fan2
[7 empty] | 3F | 63 | 0B 41; |  | Fan3 |  | tag1_fan3
[7 empty] | 40 | 64 | 11 41; |  | Auto |  | tag1_auto
[7 empty] | 41 | 65 | 17 41; |  | Eco |  | tag1_eco
[7 empty] | 42 | 66 | 1D 41; |  | Off |  | tag1_off
[7 empty] | 43 | 67 | 00 00; |  | Input 1 on
[7 empty] | 44 | 68 | 00 00; |  | Input 1 off
[7 empty] | 45 | 69 | 00 00; |  | Input 2 on
[7 empty] | 46 | 70 | 3B 01; |  | Input 2 off |  | tag1_unpress
[7 empty] | 47 | 71 | 00 00; |  | Dummy
[7 empty] | 48 | 72 | 34 01; |  | Press no right |  | tag1_resetsetpoint
[7 empty] | 49 | 73 | 2C 00; | IOEXP1 | OffLine |  | dev_offline
[7 empty] | 4A | 74 | 00 00; |  | Input | 1 on
[7 empty] | 4B | 75 | 00 00; |  | Input | 1 off
[7 empty] | 4C | 76 | 00 00; |  | Input | 2 on
[7 empty] | 4D | 77 | 00 00; |  | Input | 2 off
[7 empty] | 4E | 78 | 00 00; |  | Input | 3 on
[7 empty] | 4F | 79 | 00 00; |  | Input | 3 off
[7 empty] | 50 | 80 | 00 00; |  | Input | 4 on
[7 empty] | 51 | 81 | 00 00; |  | Input | 4 off
[7 empty] | 52 | 82 | 00 00; |  | Input | 5 on
[7 empty] | 53 | 83 | 00 00; |  | Input | 5 off
[7 empty] | 54 | 84 | 00 00; |  | Input | 6 on
[7 empty] | 55 | 85 | 00 00; |  | Input | 6 off
[7 empty] | 56 | 86 | 00 00; |  | Input | 7 on
[7 empty] | 57 | 87 | 00 00; |  | Input | 7 off
[7 empty] | 58 | 88 | 00 00; |  | Input | 8 on
[7 empty] | 59 | 89 | 00 00; |  | Input | 8 off
[7 empty] | 5A | 90 | 00 00; | IODEXP | OffLine
[7 empty] | 5B | 91 | 2C 00; | TAG2 | OffLine |  | dev_offline
[7 empty] | 5C | 92 | 00 00; |  | C/F
[7 empty] | 5D | 93 | 00 00;
[7 empty] | 5E | 94 | 00 00; |  | out temp
[7 empty] | 5F | 95 | 93 41; |  | Btn - |  | tag2_readsetpoint
[7 empty] | 60 | 96 | 93 41; |  | Btn + |  | tag2_readsetpoint
[7 empty] | 61 | 97 | 7A 41; |  | Fan1 |  | tag2_fan1
[7 empty] | 62 | 98 | 7D 41; |  | Fan2 |  | tag2_fan2
[7 empty] | 63 | 99 | 80 41; |  | Fan3 |  | tag2_fan3
[7 empty] | 64 | 100 | 83 41; |  | Auto |  | tag2_auto
[7 empty] | 65 | 101 | 86 41; |  | Eco |  | tag2_eco
[7 empty] | 66 | 102 | 89 41; |  | Off |  | tag2_off
[7 empty] | 67 | 103 | 00 00; |  | Input 1 on
[7 empty] | 68 | 104 | 00 00; |  | Input 1 off
[7 empty] | 69 | 105 | 00 00; |  | Input 2 on
[7 empty] | 6A | 106 | A1 01; |  | Input 2 off |  | tag2_unpress
[7 empty] | 6B | 107 | 00 00; |  | Dummy
[7 empty] | 6C | 108 | 9A 01; |  | Press no right |  | tag2_resetsetpoint
[7 empty] | 6D | 109 | 2C 00; | TAG3 | OffLine |  | dev_offline
[7 empty] | 6E | 110 | 00 00; |  | C/F
[7 empty] | 6F | 111 | 00 00;
[7 empty] | 70 | 112 | 00 00; |  | out temp
[7 empty] | 71 | 113 | C2 41; |  | Btn - |  | tag3_readsetpoint
[7 empty] | 72 | 114 | C2 41; |  | Btn + |  | tag3_readsetpoint
[7 empty] | 73 | 115 | A9 41; |  | Fan1 |  | tag3_fan1
[7 empty] | 74 | 116 | AC 41; |  | Fan2 |  | tag3_fan2
[7 empty] | 75 | 117 | AF 41; |  | Fan3 |  | tag3_fan3
[7 empty] | 76 | 118 | B2 41; |  | Auto |  | tag3_auto
[7 empty] | 77 | 119 | B5 41; |  | Eco |  | tag3_eco
[7 empty] | 78 | 120 | B8 41; |  | Off |  | tag3_off
[7 empty] | 79 | 121 | 00 00; |  | Input 1 on
[7 empty] | 7A | 122 | 00 00; |  | Input 1 off
[7 empty] | 7B | 123 | 00 00; |  | Input 2 on
[7 empty] | 7C | 124 | D0 01; |  | Input 2 off |  | tag3_unpress
[7 empty] | 7D | 125 | 00 00; |  | Dummy
[7 empty] | 7E | 126 | C9 01; |  | Press no right |  | tag3_resetsetpoint
[7 empty] | 7F | 127 | 2C 00; | TAG4 | OffLine |  | dev_offline
[7 empty] | 80 | 128 | 00 00; |  | C/F
[7 empty] | 81 | 129 | 00 00;
[7 empty] | 82 | 130 | 00 00; |  | out temp
[7 empty] | 83 | 131 | F1 41; |  | Btn - |  | tag4_readsetpoint
[7 empty] | 84 | 132 | F1 41; |  | Btn + |  | tag4_readsetpoint
[7 empty] | 85 | 133 | D8 41; |  | Fan1 |  | tag4_fan1
[7 empty] | 86 | 134 | DB 41; |  | Fan2 |  | tag4_fan2
[7 empty] | 87 | 135 | DE 41; |  | Fan3 |  | tag4_fan3
[7 empty] | 88 | 136 | E1 41; |  | Auto |  | tag4_auto
[7 empty] | 89 | 137 | E4 41; |  | Eco |  | tag4_eco
[7 empty] | 8A | 138 | E7 41; |  | Off |  | tag4_off
[7 empty] | 8B | 139 | 00 00; |  | Input 1 on
[7 empty] | 8C | 140 | 00 00; |  | Input 1 off
[7 empty] | 8D | 141 | 00 00; |  | Input 2 on
[7 empty] | 8E | 142 | FF 01; |  | Input 2 off |  | tag4_unpress
[7 empty] | 8F | 143 | 00 00; |  | Dummy
[7 empty] | 90 | 144 | F8 01; |  | Press no right |  | tag4_resetsetpoint
[7 empty] | 91 | 145 | 2C 00; | TAG5 | OffLine |  | dev_offline
[7 empty] | 92 | 146 | 00 00; |  | C/F
[7 empty] | 93 | 147 | 00 00;
[7 empty] | 94 | 148 | 00 00; |  | out temp
[7 empty] | 95 | 149 | 20 42; |  | Btn - |  | tag5_readsetpoint
[7 empty] | 96 | 150 | 20 42; |  | Btn + |  | tag5_readsetpoint
[7 empty] | 97 | 151 | 07 42; |  | Fan1 |  | tag5_fan1
[7 empty] | 98 | 152 | 0A 42; |  | Fan2 |  | tag5_fan2
[7 empty] | 99 | 153 | 0D 42; |  | Fan3 |  | tag5_fan3
[7 empty] | 9A | 154 | 10 42; |  | Auto |  | tag5_auto
[7 empty] | 9B | 155 | 13 42; |  | Eco |  | tag5_eco
[7 empty] | 9C | 156 | 16 42; |  | Off |  | tag5_off
[7 empty] | 9D | 157 | 00 00; |  | Input 1 on
[7 empty] | 9E | 158 | 00 00; |  | Input 1 off
[7 empty] | 9F | 159 | 00 00; |  | Input 2 on
[7 empty] | A0 | 160 | 2E 02; |  | Input 2 off |  | tag5_unpress
[7 empty] | A1 | 161 | 00 00; |  | Dummy
[7 empty] | A2 | 162 | 27 02; |  | Press no right |  | tag5_resetsetpoint
[7 empty] | A3 | 163 | 2C 00; | TAG6 | OffLine |  | dev_offline
[7 empty] | A4 | 164 | 00 00; |  | C/F
[7 empty] | A5 | 165 | 00 00;
[7 empty] | A6 | 166 | 00 00; |  | out temp
[7 empty] | A7 | 167 | 61 42; |  | Btn - |  | tag6_readsetpoint
[7 empty] | A8 | 168 | 61 42; |  | Btn + |  | tag6_readsetpoint
[7 empty] | A9 | 169 | 36 42; |  | Fan1 |  | tag6_fan1
[7 empty] | AA | 170 | 3C 42; |  | Fan2 |  | tag6_fan2
[7 empty] | AB | 171 | 42 42; |  | Fan3 |  | tag6_fan3
[7 empty] | AC | 172 | 48 42; |  | Auto |  | tag6_auto
[7 empty] | AD | 173 | 4E 42; |  | Eco |  | tag6_eco
[7 empty] | AE | 174 | 54 42; |  | Off |  | tag6_off
[7 empty] | AF | 175 | 00 00; |  | Input 1 on
[7 empty] | B0 | 176 | 00 00; |  | Input 1 off
[7 empty] | B1 | 177 | 00 00; |  | Input 2 on
[7 empty] | B2 | 178 | 72 02; |  | Input 2 off |  | tag6_unpress
[7 empty] | B3 | 179 | 00 00; |  | Dummy
[7 empty] | B4 | 180 | 6B 02; |  | Press no right |  | tag6_resetsetpoint
[7 empty] | B5 | 181 | 2C 00; | GSW02 A | OffLine |  | dev_offline
[7 empty] | B6 | 182 | 00 00; |  | Button | 1 on
[7 empty] | B7 | 183 | 00 00; |  | Button | 1 off
[7 empty] | B8 | 184 | 00 00; |  | Button | 2 on
[7 empty] | B9 | 185 | 00 00; |  | Button | 2 off
[7 empty] | BA | 186 | 00 00; |  | Button | 3 on
[7 empty] | BB | 187 | 00 00; |  | Button | 3 off
[7 empty] | BC | 188 | C3 04; |  | Button | 4 on | gsw02a_btn_4
[7 empty] | BD | 189 | 00 00; |  | Button | 4 off
[7 empty] | BE | 190 | 00 00; |  | Button | 5 on
[7 empty] | BF | 191 | 00 00; |  | Button | 5 off
[7 empty] | C0 | 192 | CC 04; |  | Button | 6 on | gsw02a_btn_6
[7 empty] | C1 | 193 | 00 00; |  | Button | 6 off
[7 empty] | C2 | 194 | 00 00; |  | Button | 7 on
[7 empty] | C3 | 195 | 00 00; |  | Button | 7 off
[7 empty] | C4 | 196 | 00 00; |  | Button | 8 on
[7 empty] | C5 | 197 | 00 00; |  | Button | 8 off
[7 empty] | C6 | 198 | 00 00; |  | Button | 9 on
[7 empty] | C7 | 199 | 00 00; |  | Button | 9 off
[7 empty] | C8 | 200 | 00 00; |  | Button | 10 on
[7 empty] | C9 | 201 | 00 00; |  | Button | 10 off
[7 empty] | CA | 202 | 00 00; |  | Button | 11 on
[7 empty] | CB | 203 | 00 00; |  | Button | 11 off
[7 empty] | CC | 204 | 00 00; |  | Button | 12 on
[7 empty] | CD | 205 | 00 00; |  | Button | 12 off
[7 empty] | CE | 206 | 00 00; |  | motion | 13 on
[7 empty] | CF | 207 | 00 00; |  | motion | 13 off
[7 empty] | D0 | 208 | 2C 00; | GSW01 | OffLine |  | dev_offline
[7 empty] | D1 | 209 | 00 00; |  | Button | 1 on
[7 empty] | D2 | 210 | 00 00; |  | Button | 1 off
[7 empty] | D3 | 211 | 00 00; |  | Button | 2 on
[7 empty] | D4 | 212 | 00 00; |  | Button | 2 off
[7 empty] | D5 | 213 | 00 00; |  | Button | 3 on
[7 empty] | D6 | 214 | 00 00; |  | Button | 3 off
[7 empty] | D7 | 215 | 00 00; |  | Button | 4 on
[7 empty] | D8 | 216 | 00 00; |  | Button | 4 off
[7 empty] | D9 | 217 | D2 04; |  | Button | 5 on | gsw01_btn_5
[7 empty] | DA | 218 | 00 00; |  | Button | 5 off
[7 empty] | DB | 219 | 00 00; |  | Button | 6 on
[7 empty] | DC | 220 | 00 00; |  | Button | 6 off
[7 empty] | DD | 221 | 00 00; |  | Button | 7 on
[7 empty] | DE | 222 | 00 00; |  | Button | 7 off
[7 empty] | DF | 223 | 00 00; |  | Button | 8 on
[7 empty] | E0 | 224 | 00 00; |  | Button | 8 off
[7 empty] | E1 | 225 | 00 00; |  | Button | 9 on
[7 empty] | E2 | 226 | 00 00; |  | Button | 9 off
[7 empty] | E3 | 227 | 00 00; |  | Button | 10 on
[7 empty] | E4 | 228 | 00 00; |  | Button | 10 off
[7 empty] | E5 | 229 | 00 00; |  | Button | 11 on
[7 empty] | E6 | 230 | 00 00; |  | Button | 11 off
[7 empty] | E7 | 231 | 00 00; |  | Button | 12 on
[7 empty] | E8 | 232 | 00 00; |  | Button | 12 off
[7 empty] | E9 | 233 | 00 00; |  | motion | 13 on
[7 empty] | EA | 234 | 00 00; |  | motion | 13 off
[7 empty] | EB | 235 | 2C 00; | Temp-Hub1 | OffLine |  | dev_offline
[7 empty] | EC | 236 | 2C 00; | Temp-Hub2 | OffLine |  | dev_offline
[7 empty] | ED | 237 | 2C 00; | Temp-Hub3 | OffLine |  | dev_offline
[7 empty] | EE | 238 | 2C 00; | Temp-Hub4 | OffLine |  | dev_offline
[7 empty] | EF | 239 | 2C 00; | Temp-Hub5 | OffLine |  | dev_offline
[7 empty] | F0 | 240 | 2C 00; | Temp-Hub6 | OffLine |  | dev_offline
[7 empty] | F1 | 241 | 00 00; | Temp-Hub7 | OffLine
[7 empty] | F2 | 242 | 00 00; | Vingcard | OffLine
[7 empty] | F3 | 243 | A9 00; |  | Egress handle |  | door_egress
[7 empty] | F4 | 244 | 00 00; |  | Open aux
[7 empty] | F5 | 245 | 00 00; |  | Ajar start @ 5min
[7 empty] | F6 | 246 | A6 00; |  | Ajar end |  | door_close
[7 empty] | F7 | 247 | 47 00; |  | Card entry |  | cardok_idpg
[7 empty] | F8 | 248 | 00 00; |  | DND ON |  |  | vingcard_dnd_on
[7 empty] | F9 | 249 | 00 00; |  | DND OFF |  |  | vingcard_dnd_off
[7 empty] | FA | 250 | 8F 00; |  | Card reject |  | cardnok_idpg
[7 empty] | FB | 251 | 00 00;
[7 empty] | FC | 252 | 00 00;
[7 empty] | FD | 253 | 00 00;
[7 empty] | FE | 254 | 00 00;
[7 empty] | FF | 255 | 00 00;
[7 empty] | 100 | 256 | 00 00;
[7 empty] | 101 | 257 | 00 00; | RCU2 slave1 | Watchdog
[7 empty] | 102 | 258 | 00 00; |  | ModBus Reg0
[7 empty] | 103 | 259 | 90 02; |  | ModBus Reg1 |  | receive_rcu2_workflow
[7 empty] | 104 | 260 | A0 02; |  | ModBus Reg2 |  | receive_rcu2_relays
[7 empty] | 105 | 261 | A4 02; |  | ModBus Reg3 |  | receive_rcu2_bed1_panel
[7 empty] | 106 | 262 | AB 02; |  | ModBus Reg4 |  | receive_rcu2_bed2_panel
[7 empty] | 107 | 263 | B0 02; |  | ModBus Reg5 |  | receive_rcu2_bed3_panel
[7 empty] | 108 | 264 | C5 02; |  | ModBus Reg6 |  | receive_rcu2_bath2_panel
[7 empty] | 109 | 265 | C9 02; |  | ModBus Reg7 |  | receive_rcu2_bath3_panel
[7 empty] | 10A | 266 | CD 02; |  | ModBus Reg8 |  | receive_rcu2_master_bath_panel
[7 empty] | 10B | 267 | B5 02; |  | ModBus Reg9 |  | receive_rcu2_master_bed_panel
[7 empty] | 10C | 268 | 9C 02; |  | ModBus Reg10 |  | receive_rcu2_notifications
[7 empty] | 10D | 269 | 00 00; |  | ModBus Reg11
[7 empty] | 10E | 270 | 00 00; |  | ModBus Reg12
[7 empty] | 10F | 271 | 00 00; |  | ModBus Reg13
[7 empty] | 110 | 272 | 00 00; |  | ModBus Reg14
[7 empty] | 111 | 273 | 00 00; |  | ModBus Reg15
[7 empty] | 112 | 274 | 00 00; | RCU3 slave2 | Watchdog
[7 empty] | 113 | 275 | 00 00; |  | ModBus Reg0
[7 empty] | 114 | 276 | 96 02; |  | ModBus Reg1 |  | receive_rcu3_workflow
[7 empty] | 115 | 277 | A2 02; |  | ModBus Reg2 |  | receive_rcu3_relays
[7 empty] | 116 | 278 | BC 02; |  | ModBus Reg3 |  | receive_rcu3_master_bed_panel
[7 empty] | 117 | 279 | D1 02; |  | ModBus Reg4 |  | receive_rcu3_entrance_panel
[7 empty] | 118 | 280 | A8 02; |  | ModBus Reg5 |  | receive_rcu3_bed1_panel
[7 empty] | 119 | 281 | C1 02; |  | ModBus Reg6 |  | receive_rcu3_bath1_panel
[7 empty] | 11A | 282 | D8 02; |  | ModBus Reg7 |  | receive_rcu3_corridor_panel
[7 empty] | 11B | 283 | DD 02; |  | ModBus Reg8 |  | receive_rcu3_motion
[7 empty] | 11C | 284 | B8 02; |  | ModBus Reg9 |  | receive_rcu3_notifications
[7 empty] | 11D | 285 | 00 00; |  | ModBus Reg10
[7 empty] | 11E | 286 | 00 00; |  | ModBus Reg11
[7 empty] | 11F | 287 | 00 00; |  | ModBus Reg12
[7 empty] | 120 | 288 | 00 00; |  | ModBus Reg13
[7 empty] | 121 | 289 | 00 00; |  | ModBus Reg14
[7 empty] | 122 | 290 | 00 00; |  | ModBus Reg15
[7 empty] | 123 | 291 | 00 00; | RCU4 slave3 | Watchdog
[7 empty] | 124 | 292 | 00 00; |  | ModBus Reg0
[7 empty] | 125 | 293 | 00 00; |  | ModBus Reg1
[7 empty] | 126 | 294 | 00 00; |  | ModBus Reg2
[7 empty] | 127 | 295 | E3 02; |  | ModBus Reg3 |  | receive_rcu4_fcu_speed
[7 empty] | 128 | 296 | E5 02; |  | ModBus Reg4 |  | receive_rcu4_fcu_setpoint
[7 empty] | 129 | 297 | E8 02; |  | ModBus Reg5 |  | receive_rcu4_fcu_current_temp
[7 empty] | 12A | 298 | 00 00; |  | ModBus Reg6
[7 empty] | 12B | 299 | EB 02; |  | ModBus Reg7 |  | receive_rcu4_PT100_7_water_return
[7 empty] | 12C | 300 | EE 02; |  | ModBus Reg8 |  | receive_rcu4_PT100_7_water_supply
[7 empty] | 12D | 301 | F1 02; |  | ModBus Reg9 |  | receive_rcu4_PT100_7_air_return
[7 empty] | 12E | 302 | F4 02; |  | ModBus Reg10 |  | receive_rcu4_PT100_7_air_supply
[7 empty] | 12F | 303 | DF 02; |  | ModBus Reg11 |  | receive_rcu4_notifications
[7 empty] | 130 | 304 | 00 00; |  | ModBus Reg12
[7 empty] | 131 | 305 | 00 00; |  | ModBus Reg13
[7 empty] | 132 | 306 | 00 00; |  | ModBus Reg14
[7 empty] | 133 | 307 | 00 00; |  | ModBus Reg15

## XCODE1
XCODE [0.9,2]
0 | #startup
1 | version [35561452341814213551145390817034,9]
2 | goto #debugging
3 | reserved for ipad
4 | reserved for ipad
5 | reserved for ipad
6 | reserved for ipad
7 | reserved for ipad
8 | reserved for ipad
9 | reserved for ipad
10 | reserved for ipad
11 | reserved for ipad
12 | reserved for ipad
13 | reserved for ipad
14 | reserved for ipad
15 | reserved for ipad
16 | reserved for ipad
17 | reserved for ipad
18 | reserved for ipad
19 | reserved for ipad
20 | reserved for ipad
21 | reserved for ipad
22 | reserved for ipad
23 | goto #checkout
24 | goto #checkin
25
26 | function startup
27 | send.modbus $dev=server $reg=0 $dec=0
28 | send.modbus $type=idpg $reg=6 $dec=70*10 //green
29 | send.modbus $type=idpg $reg=83 $dec=100*10 //red
30 | send.modbus $type=tag $reg=15 $dec=50*10 //button interactive
31 | send.modbus $type=tag $reg=16 $dec=5*10 //button non-interactive
32 | send.modbus $type=tag $reg=17 $dec=80*10 //display interactive
33 | send.modbus $type=tag $reg=18 $dec=5*10 //display non-interactive
34 | send.modbus $type=gsw $reg=15 $dec=80*10
35 | send.modbus $type=gsw $reg=16 $dec=30*10
36 | run #refresh_idpg $sec=2
37 | run #tag_flash $sec=15
38 | reuse #dnd_relay $sec=5
39 | reuse #temp_probe_cycle $min=1
40 | reuse #power_recover $sec=5
41 | exit
42
43
44 | function debugging
45 | debug
46 | exit
47
48
49 | function thermo_cycle
50 | send.modbus $dev=server $reg=14 $len=16
51 | exit
52
53 | function dev_offline
54 | send.modbus $dev=server $reg=8 $len=4
55 | exit
56
57
58
59
60 | function refresh_idpg
61 | load $var=workflow
62 | 0x10 80 0c 00 04 06 0a 00//Array table colors/blink
63 | send.modbus $dev=idpg $reg=4 $len=4
64 | load $var=workflow
65 | 0x10 80 0c 00 01 08 0a 00//Array table blink time
66 | send.modbus $dev=idpg $reg=7 $len=2
67 | exit
68 | 0x00 54 00 00 55 54 00 00 // Data1 ColorBlink
69 | 0x14 54 0f 00 14 54 00 00 // Data2 ColorBlink
70 | 0x55 54 00 00 41 54 00 00 // Data3 ColorBlink
71 | 0xeb 54 00 00 aa a0 00 00 // Data4 ColorBlink
72 | 0xaa a2 0f 00 ff 54 0f 00 // Data5 ColorBlink
73 | 0x00 18 18 00 00 00 00 00 // Data1 Blink time (ex 0 18)
74 | 0x05 0a 00 00 00 00 00 00 // Data2 Blink time (ex 0 18)
75 | exit
76
77
78
79
80
81
82
83 | function bell_idpg | ok
84 | load $var=workflow
85 | if equal goto #+3 $dec=1
86 | load $dec=0
87 | goto #+2
88 | load $hex=5040
89 | send.modbus $dev=idpg $reg=4 $len=4
90 | reuse #idpg_relay_bell
91 | wait $sec=1
92 | reuse #refresh_idpg
93 | exit
94
95
96
97 | function cardOK_idpg
98 | send.modbus $dev=server $reg=15 $hex=0001 //Door open/Ingress (Door open from outside with Lock)
99 | reuse #set_lock_action
100 | send.modbus $dev=idpg $reg=4 $hex=5555
101 | math.and $hex=ff
102 | if equal #+3 $hex=1 //set as staff
103 | function door_contact_override_guest
104 | load $hex=1 //otherwise user
105 | goto #+2
106 | function door_contact_override_staff
107 | load $hex=10 //staff
108 | send.modbus $dev=server $reg=6 $len=16
109 | load $hex=1 //always user
110 | save $var=temp_user
111 | reuse #refresh_idpg $sec=1
112 | load $var=user
113 | if equal goto #exit $var=temp_user
114 | user.set $var=temp_user
115 | send.modbus $dev=2 $reg=5 $len=2 //rcu2 user
116 | send.modbus $dev=3 $reg=5 $len=2 //rcu3 user
117 | send.modbus $dev=4 $reg=5 $len=2 //rcu4 user
118 | load $hex=0 // new payload cause and intterrupt
119 | send.modbus $dev=server $reg=2 $len=16
120 | season.set $hex=11 //summer + min fan speed
121 | load $var=user
122 | if equal #staff_welcome $hex=10 //goto staff welcome scene
123 | rcu2_relays.or $relay=10,13-16
124 | send.modbus $dev=2 $reg=7 $len=2
125 | rcu3_relays.or $relay=8
126 | send.modbus $dev=3 $reg=7 $len=2
127 | rcu4_relays.or $relay=4,5,15,16
128 | send.modbus $dev=4 $reg=7 $len=2
129 | goto #common_welcome
130 | function staff_welcome
131 | rcu2_relays.or $relay=1-16
132 | send.modbus $dev=2 $reg=7 $len=2
133 | rcu3_relays.or $relay=1-16
134 | send.modbus $dev=3 $reg=7 $len=2
135 | rcu4_relays.or $relay=4-7,9-16
136 | send.modbus $dev=4 $reg=7 $len=2
137 | function common_welcome
138 | function tag_conditional_check_with_user
139 | load $var=temp2
140 | send.modbus $dev=tag2 $reg=25 $len=2
141 | reuse #refresh_tag2 $dev=tag2
142 | load $var=temp3
143 | send.modbus $dev=tag3 $reg=25 $len=2
144 | reuse #refresh_tag3 $dev=tag3
145 | load $var=temp4
146 | send.modbus $dev=tag4 $reg=25 $len=2
147 | reuse #refresh_tag4 $dev=tag4
148 | load $var=temp5
149 | send.modbus $dev=tag5 $reg=25 $len=2
150 | reuse #refresh_tag5 $dev=tag5
151 | function wc_tag_refresh_with_user
152 | rcu.read input
153 | math.xor $bit=2
154 | if bit true #exit $bit=2
155 | load $var=temp1
156 | send.modbus $dev=tag1 $reg=25 $len=2
157 | load $var=temp6
158 | send.modbus $dev=tag6 $reg=25 $len=2
159 | reuse #refresh_tag1 $dev=tag1
160 | reuse #refresh_tag6 $dev=tag6
161 | exit
162
163
164 | function cardNOK_idpg
165 | send.modbus $dev=server $reg=5 $len=16
166 | send.modbus $dev=idpg $reg=4 $hex=aaaa
167 | reuse #refresh_idpg $sec=1
168 | exit
169
170
171 | function idpg_relay_bell | ok
172 | send.modbus $dev=4 $reg=11 $len=2 $hex=1
173 | exit
174
175
176
177 | function set_lock_action
178 | lockaction.set $dec=1
179 | reuse #unset_lock_action $sec=60
180 | exit
181
182 | function unset_lock_action
183 | lockaction.unset
184 | exit
185
186
187
188 | function door_open
189 | load $var=lockaction
190 | if not equal #exit $hex=0
191 | send.modbus $dev=server $reg=15 $hex=0004 //Door contact open, sence of no direction (only for door contact)
192 | load $var=checkin
193 | if equal #door_contact_override_guest $dec=1
194 | goto #door_contact_override_staff
195 | exit
196
197
198 | function door_contact_close
199 | load $var=lockaction
200 | if not equal #exit $hex=0
201 | function door_close
202 | send.modbus $dev=server $reg=15 $hex=0000 //Door close/ajar end (for Door contact also)
203 | reuse #door_close_delayed $sec=10
204 | exit
205
206
207 | function door_egress
208 | send.modbus $dev=server $reg=15 $hex=0000 //Door close/ajar end (for Door contact also)
209 | reuse #door_close_delayed $sec=10
210 | exit
211
212
213
214 | function door_close_delayed
215 | last_action.set $dec=0
216 | reuse #check_exit_scene $sec=20 $dev=tag1
217 | exit
218
219
220
221 | function checkout
222 | load $hex=2 // advance user absence by checkout , cause and interrupt mode
223 | send.modbus $dev=server $reg=3 $len=16 //User absence
224 | rcu2_relays.unset $relay=15,16
225 | send.modbus $dev=2 $reg=7 $len=2 //rcu2 relays
226 | function checkout_common
227 | send.modbus $dev=4 $reg=9 $len=2 $var=thermo1 //tag7 fan
228 | send.modbus $dev=4 $reg=10 $len=2 $var=temp1 //tag7 temp
229 | wait $sec=2
230 | load $dec=0
231 | save $var=user,temp_user,workflow
232 | save $var=rcu3_relays,rcu4_relays
233 | send.modbus $dev=2 $reg=6 $len=2 //workflow RCU2
234 | wait $sec=0.15
235 | send.modbus $dev=3 $reg=6 $len=2 //workflow RCU3
236 | send.modbus $dev=server $reg=4 $len=3
237 | send.modbus $dev=2 $reg=5 $len=2 //rcu2 user
238 | wait $sec=0.15
239 | send.modbus $dev=3 $reg=5 $len=2 //rcu3 user
240 | send.modbus $dev=4 $reg=5 $len=2 //rcu4 user
241 | season.set $hex=01 //summer - min fan speed
242 | rcu2_relays.and $relay=1-14
243 | send.modbus $dev=2 $reg=7 $len=2 //rcu2 relays
244 | send.modbus $dev=3 $reg=7 $len=2 $hex=0//unset rcu3 relays
245 | send.modbus $dev=4 $reg=7 $len=2 $hex=0//unset rcu4 relays
246 | reuse #refresh_idpg
247 | reuse #dnd_relay
248 | goto #tag_conditional_check_without_user
249 | exit
250
251
252
253
254 | function checkin
255 | load $hex=1 // advance user absence by checkin , cause and interrupt mode
256 | send.modbus $dev=server $reg=3 $len=16 //User absence
257 | rcu2_relays.set $relay=15,16
258 | send.modbus $dev=2 $reg=7 $len=2 //rcu2 relays
259 | goto #checkout_common
260 | exit
261
262
263
264
265
266 | function tag_flash
267 | load $var=tag_minmax
268 | if not equal #+3 $hex=0
269 | tag_minmax.set $dec=19*256+28
270 | send.modbus $type=tag $reg=6 $len=2
271 | //load $dec=24*10
272 | //save $var=temp1,temp2,temp3,temp4,temp5,temp6
273 | //send.modbus $type=tag $reg=25 $len=2
274 | //load $fan=fan1
275 | //save $var=thermo1,thermo2,thermo3,thermo4,thermo5,thermo6
276 | reuse #min_fan_speed_check
277 | //room_empty.set $hex=8014
278 | anti_ice.set $dec=65536*35*10+5*10
279 | intervention.set $dec=65536*0.5*10+0.1*10
280 | send.modbus $type=tag $reg=3 $dec=2 //disable top buttons
281 | wait $sec=0.01
282 | send.modbus $type=tag $reg=8 $hex=2 //TAGs +/- steps 0.5 degrees
283 | load $var=user
284 | if bit true #+3 $hex=ff
285 | reuse #tag_conditional_check_without_user
286 | exit
287 | reuse #tag_conditional_check_with_user
288 | exit
289
290
291
292 | function min_fan_speed_check
293 | load $var=user
294 | if bit true #+4 $hex=ff
295 | season.set $hex=01 //summer - min fan speed
296 | exit
297 | season.set $hex=11 //summer + min fan speed
298 | exit
299
300
301
302 | run #bedroom_master @rcu2
303
304
305
306
307
308 | function refresh_tag1
309 | load $var=thermo1
310 | math.and $hex=aaaa
311 | if equal #+2 $hex=80
312 | math.shiftR $dec=1
313 | send.modbus $dev=tag1 $reg=13 $len=4
314 | exit
315
316 | function tag1_fan1
317 | rcu.read input
318 | math.xor $bit=2
319 | if bit true #exit $bit=2
320 | send.modbus $dev=server $reg=13 $hex=0001
321 | load $fan=fan1
322 | goto #tag1_common
323
324 | function tag1_fan2
325 | rcu.read input
326 | math.xor $bit=2
327 | if bit true #exit $bit=2
328 | send.modbus $dev=server $reg=13 $hex=0002
329 | load $fan=fan2
330 | goto #tag1_common
331
332 | function tag1_fan3
333 | rcu.read input
334 | math.xor $bit=2
335 | if bit true #exit $bit=2
336 | send.modbus $dev=server $reg=13 $hex=0003
337 | load $fan=fan3
338 | goto #tag1_common
339
340 | function tag1_auto
341 | rcu.read input
342 | math.xor $bit=2
343 | if bit true #exit $bit=2
344 | send.modbus $dev=server $reg=13 $hex=0004
345 | load $fan=auto
346 | goto #tag1_common
347
348 | function tag1_eco
349 | rcu.read input
350 | math.xor $bit=2
351 | if bit true #exit $bit=2
352 | send.modbus $dev=server $reg=13 $hex=0005
353 | load $fan=eco
354 | goto #tag1_common
355
356 | function tag1_off
357 | rcu.read input
358 | math.xor $bit=2
359 | if bit true #exit $bit=2
360 | send.modbus $dev=server $reg=13 $hex=0006
361 | load $fan=off
362 | function tag1_common
363 | save $var=thermo1
364 | send.modbus $dev=tag1 $reg=13 $len=4
365 | reuse #refresh_tag1 $sec=15
366 | exit
367
368 | function tag1_wakeup
369 | load $var=thermo1
370 | send.modbus $dev=tag1 $reg=13 $len=4
371 | reuse #refresh_tag1 $sec=15
372 | exit
373
374 | function tag1_readsetpoint
375 | rcu.read input
376 | math.xor $bit=2
377 | if bit true #exit $bit=2
378 | reuse #tag1_wakeup
379 | wait $sec=6
380 | read.modbus $dev=tag1 $reg=25
381 | save $var=temp1
382 | load shift enum
383 | send.modbus $dev=server $reg=11 $len=8
384 | exit
385
386 | function tag1_resetsetpoint
387 | wait $sec=2
388 | load $var=room_empty
389 | if less than #+3 $hex=8000
390 | math.and $relay=16
391 | math.add $var=temp1
392 | send.modbus $dev=tag1 $reg=25 $len=2
393 | exit
394
395
396 | function tag1_unpress
397 | load $hex=1 // cause and interrupt for GS
398 | goto #set_last_action
399
400
401
402 | function window_open
403 | send.modbus $dev=server $reg=12 $hex=001
404 | wait $sec=0.01
405 | send.modbus $dev=server $reg=12 $hex=501
406 | reuse #refresh_tag1 $dev=tag1
407 | reuse #refresh_tag6 $dev=tag6
408 | reuse #delay_window_open $sec=5
409 | exit
410
411
412 | function delay_window_open
413 | rcu.read input
414 | if bit true #exit $bit=2
415 | load $var=thermo1
416 | if equal #exit $hex=2000
417 | backup_thermo1.set $var=thermo1
418 | backup_thermo6.set $var=thermo6
419 | send.modbus $dev=tag1 $reg=3 $hex=6 //TAG1 disable +/- & top button
420 | wait $sec=0.01
421 | send.modbus $dev=tag6 $reg=3 $hex=6 //TAG6 disable +/- & top button
422 | load $hex=2000
423 | save $var=thermo1,thermo6
424 | rcu.dim aout1 $lum=0% $sec=0.5
425 | load dimmer $lum=0% $sec=0.5
426 | send.dimmer $dev=ioexp2 $ch=1
427 | load $hex=8
428 | send.modbus $dev=tag1 $reg=13 $len=4
429 | send.modbus $dev=tag6 $reg=13 $len=4
430 | exit
431
432
433 | function window_close
434 | send.modbus $dev=server $reg=12 $hex=000
435 | wait $sec=0.01
436 | send.modbus $dev=server $reg=12 $hex=500
437 | reuse #delay_window_close $sec=5
438 | exit
439
440
441 | function delay_window_close
442 | rcu.read input
443 | math.xor $bit=2
444 | if bit true #exit $bit=2
445 | load $var=thermo1
446 | if not equal #exit $hex=2000
447 | thermo1.set $var=backup_thermo1
448 | thermo6.set $var=backup_thermo6
449 | send.modbus $dev=tag1 $reg=3 $hex=2 //TAG1 disable top button
450 | wait $sec=0.01
451 | send.modbus $dev=tag6 $reg=3 $hex=2 //TAG6 disable top button
452 | load $var=user
453 | if not equal #+5 $hex=0
454 | load $hex=80
455 | send.modbus $dev=tag1 $reg=13 $len=4
456 | send.modbus $dev=tag6 $reg=13 $len=4
457 | exit
458 | reuse #refresh_tag1 $dev=tag1
459 | reuse #refresh_tag6 $dev=tag6
460 | exit
461
462
463
464
465
466
467 | function refresh_tag2
468 | load $var=thermo2
469 | math.and $hex=aaaa
470 | if equal #+2 $hex=80
471 | math.shiftR $dec=1
472 | send.modbus $dev=tag2 $reg=13 $len=4
473 | exit
474
475 | function tag2_fan1
476 | send.modbus $dev=server $reg=13 $hex=0101
477 | load $fan=fan1
478 | goto #tag2_common
479
480 | function tag2_fan2
481 | send.modbus $dev=server $reg=13 $hex=0102
482 | load $fan=fan2
483 | goto #tag2_common
484
485 | function tag2_fan3
486 | send.modbus $dev=server $reg=13 $hex=0103
487 | load $fan=fan3
488 | goto #tag2_common
489
490 | function tag2_auto
491 | send.modbus $dev=server $reg=13 $hex=0104
492 | load $fan=auto
493 | goto #tag2_common
494
495 | function tag2_eco
496 | send.modbus $dev=server $reg=13 $hex=0105
497 | load $fan=eco
498 | goto #tag2_common
499
500 | function tag2_off
501 | send.modbus $dev=server $reg=13 $hex=0106
502 | load $fan=off
503 | function tag2_common
504 | save $var=thermo2
505 | send.modbus $dev=tag2 $reg=13 $len=4
506 | reuse #refresh_tag2 $sec=15
507 | exit
508
509 | function tag2_wakeup
510 | load $var=thermo2
511 | send.modbus $dev=tag2 $reg=13 $len=4
512 | reuse #refresh_tag2 $sec=15
513 | exit
514
515 | function tag2_readsetpoint
516 | reuse #tag2_wakeup
517 | wait $sec=6
518 | read.modbus $dev=tag2 $reg=25
519 | save $var=temp2
520 | load shift enum
521 | send.modbus $dev=server $reg=11 $len=8
522 | exit
523
524 | function tag2_resetsetpoint
525 | wait $sec=2
526 | load $var=room_empty
527 | if less than #+3 $hex=8000
528 | math.and $relay=16
529 | math.add $var=temp2
530 | send.modbus $dev=tag2 $reg=25 $len=2
531 | exit
532
533
534 | function tag2_unpress
535 | load $hex=1 // cause and interrupt for GS
536 | goto #set_last_action
537
538
539
540
541
542 | function refresh_tag3
543 | load $var=thermo3
544 | math.and $hex=aaaa
545 | if equal #+2 $hex=80
546 | math.shiftR $dec=1
547 | send.modbus $dev=tag3 $reg=13 $len=4
548 | exit
549
550 | function tag3_fan1
551 | send.modbus $dev=server $reg=13 $hex=0201
552 | load $fan=fan1
553 | goto #tag3_common
554
555 | function tag3_fan2
556 | send.modbus $dev=server $reg=13 $hex=0202
557 | load $fan=fan2
558 | goto #tag3_common
559
560 | function tag3_fan3
561 | send.modbus $dev=server $reg=13 $hex=0203
562 | load $fan=fan3
563 | goto #tag3_common
564
565 | function tag3_auto
566 | send.modbus $dev=server $reg=13 $hex=0204
567 | load $fan=auto
568 | goto #tag3_common
569
570 | function tag3_eco
571 | send.modbus $dev=server $reg=13 $hex=0205
572 | load $fan=eco
573 | goto #tag3_common
574
575 | function tag3_off
576 | send.modbus $dev=server $reg=13 $hex=0206
577 | load $fan=off
578 | function tag3_common
579 | save $var=thermo3
580 | send.modbus $dev=tag3 $reg=13 $len=4
581 | reuse #refresh_tag3 $sec=15
582 | exit
583
584 | function tag3_wakeup
585 | load $var=thermo3
586 | send.modbus $dev=tag3 $reg=13 $len=4
587 | reuse #refresh_tag3 $sec=15
588 | exit
589
590 | function tag3_readsetpoint
591 | reuse #tag3_wakeup
592 | wait $sec=6
593 | read.modbus $dev=tag3 $reg=25
594 | save $var=temp3
595 | load shift enum
596 | send.modbus $dev=server $reg=11 $len=8
597 | exit
598
599 | function tag3_resetsetpoint
600 | wait $sec=2
601 | load $var=room_empty
602 | if less than #+3 $hex=8000
603 | math.and $relay=16
604 | math.add $var=temp3
605 | send.modbus $dev=tag3 $reg=25 $len=2
606 | exit
607
608
609 | function tag3_unpress
610 | load $hex=1 // cause and interrupt for GS
611 | goto #set_last_action
612
613
614
615
616 | function refresh_tag4
617 | load $var=thermo4
618 | math.and $hex=aaaa
619 | if equal #+2 $hex=80
620 | math.shiftR $dec=1
621 | send.modbus $dev=tag4 $reg=13 $len=4
622 | exit
623
624 | function tag4_fan1
625 | send.modbus $dev=server $reg=13 $hex=0301
626 | load $fan=fan1
627 | goto #tag4_common
628
629 | function tag4_fan2
630 | send.modbus $dev=server $reg=13 $hex=0302
631 | load $fan=fan2
632 | goto #tag4_common
633
634 | function tag4_fan3
635 | send.modbus $dev=server $reg=13 $hex=0303
636 | load $fan=fan3
637 | goto #tag4_common
638
639 | function tag4_auto
640 | send.modbus $dev=server $reg=13 $hex=0304
641 | load $fan=auto
642 | goto #tag4_common
643
644 | function tag4_eco
645 | send.modbus $dev=server $reg=13 $hex=0305
646 | load $fan=eco
647 | goto #tag4_common
648
649 | function tag4_off
650 | send.modbus $dev=server $reg=13 $hex=0306
651 | load $fan=off
652 | function tag4_common
653 | save $var=thermo4
654 | send.modbus $dev=tag4 $reg=13 $len=4
655 | reuse #refresh_tag4 $sec=15
656 | exit
657
658 | function tag4_wakeup
659 | load $var=thermo4
660 | send.modbus $dev=tag4 $reg=13 $len=4
661 | reuse #refresh_tag4 $sec=15
662 | exit
663
664 | function tag4_readsetpoint
665 | reuse #tag4_wakeup
666 | wait $sec=6
667 | read.modbus $dev=tag4 $reg=25
668 | save $var=temp4
669 | load shift enum
670 | send.modbus $dev=server $reg=11 $len=8
671 | exit
672
673 | function tag4_resetsetpoint
674 | wait $sec=2
675 | load $var=room_empty
676 | if less than #+3 $hex=8000
677 | math.and $relay=16
678 | math.add $var=temp4
679 | send.modbus $dev=tag4 $reg=25 $len=2
680 | exit
681
682
683 | function tag4_unpress
684 | load $hex=1 // cause and interrupt for GS
685 | goto #set_last_action
686
687
688
689 | function refresh_tag5
690 | load $var=thermo5
691 | math.and $hex=aaaa
692 | if equal #+2 $hex=80
693 | math.shiftR $dec=1
694 | send.modbus $dev=tag5 $reg=13 $len=4
695 | exit
696
697 | function tag5_fan1
698 | send.modbus $dev=server $reg=13 $hex=0401
699 | load $fan=fan1
700 | goto #tag5_common
701
702 | function tag5_fan2
703 | send.modbus $dev=server $reg=13 $hex=0402
704 | load $fan=fan2
705 | goto #tag5_common
706
707 | function tag5_fan3
708 | send.modbus $dev=server $reg=13 $hex=0403
709 | load $fan=fan3
710 | goto #tag5_common
711
712 | function tag5_auto
713 | send.modbus $dev=server $reg=13 $hex=0404
714 | load $fan=auto
715 | goto #tag5_common
716
717 | function tag5_eco
718 | send.modbus $dev=server $reg=13 $hex=0405
719 | load $fan=eco
720 | goto #tag5_common
721
722 | function tag5_off
723 | send.modbus $dev=server $reg=13 $hex=0406
724 | load $fan=off
725 | function tag5_common
726 | save $var=thermo5
727 | send.modbus $dev=tag5 $reg=13 $len=4
728 | reuse #refresh_tag5 $sec=15
729 | exit
730
731 | function tag5_wakeup
732 | load $var=thermo5
733 | send.modbus $dev=tag5 $reg=13 $len=4
734 | reuse #refresh_tag5 $sec=15
735 | exit
736
737 | function tag5_readsetpoint
738 | reuse #tag5_wakeup
739 | wait $sec=6
740 | read.modbus $dev=tag5 $reg=25
741 | save $var=temp5
742 | load shift enum
743 | send.modbus $dev=server $reg=11 $len=8
744 | exit
745
746 | function tag5_resetsetpoint
747 | wait $sec=2
748 | load $var=room_empty
749 | if less than #+3 $hex=8000
750 | math.and $relay=16
751 | math.add $var=temp5
752 | send.modbus $dev=tag5 $reg=25 $len=2
753 | exit
754
755
756 | function tag5_unpress
757 | load $hex=1 // cause and interrupt for GS
758 | goto #set_last_action
759
760
761
762
763
764 | function refresh_tag6
765 | load $var=thermo6
766 | math.and $hex=aaaa
767 | if equal #+2 $hex=80
768 | math.shiftR $dec=1
769 | send.modbus $dev=tag6 $reg=13 $len=4
770 | exit
771
772 | function tag6_fan1
773 | rcu.read input
774 | math.xor $bit=2
775 | if bit true #exit $bit=2
776 | send.modbus $dev=server $reg=13 $hex=0501
777 | load $fan=fan1
778 | goto #tag6_common
779
780 | function tag6_fan2
781 | rcu.read input
782 | math.xor $bit=2
783 | if bit true #exit $bit=2
784 | send.modbus $dev=server $reg=13 $hex=0502
785 | load $fan=fan2
786 | goto #tag6_common
787
788 | function tag6_fan3
789 | rcu.read input
790 | math.xor $bit=2
791 | if bit true #exit $bit=2
792 | send.modbus $dev=server $reg=13 $hex=0503
793 | load $fan=fan3
794 | goto #tag6_common
795
796 | function tag6_auto
797 | rcu.read input
798 | math.xor $bit=2
799 | if bit true #exit $bit=2
800 | send.modbus $dev=server $reg=13 $hex=0504
801 | load $fan=auto
802 | goto #tag6_common
803
804 | function tag6_eco
805 | rcu.read input
806 | math.xor $bit=2
807 | if bit true #exit $bit=2
808 | send.modbus $dev=server $reg=13 $hex=0505
809 | load $fan=eco
810 | goto #tag6_common
811
812 | function tag6_off
813 | rcu.read input
814 | math.xor $bit=2
815 | if bit true #exit $bit=2
816 | send.modbus $dev=server $reg=13 $hex=0506
817 | load $fan=off
818 | function tag6_common
819 | save $var=thermo6
820 | send.modbus $dev=tag6 $reg=13 $len=4
821 | reuse #refresh_tag6 $sec=15
822 | exit
823
824 | function tag6_wakeup
825 | load $var=thermo6
826 | send.modbus $dev=tag6 $reg=13 $len=4
827 | reuse #refresh_tag6 $sec=15
828 | exit
829
830 | function tag6_readsetpoint
831 | rcu.read input
832 | math.xor $bit=2
833 | if bit true #exit $bit=2
834 | reuse #tag6_wakeup
835 | wait $sec=6
836 | read.modbus $dev=tag6 $reg=25
837 | save $var=temp6
838 | load shift enum
839 | send.modbus $dev=server $reg=11 $len=8
840 | exit
841
842 | function tag6_resetsetpoint
843 | wait $sec=2
844 | load $var=room_empty
845 | if less than #+3 $hex=8000
846 | math.and $relay=16
847 | math.add $var=temp6
848 | send.modbus $dev=tag6 $reg=25 $len=2
849 | exit
850
851
852 | function tag6_unpress
853 | load $hex=1 // cause and interrupt for GS
854 | goto #set_last_action
855
856
857
858
859 | function vingcard_dnd_on
860 | load $hex=7
861 | goto #2
862 | function vingcard_dnd_off
863 | load $hex=0
864 | save $var=workflow
865 | send.modbus $dev=server $reg=4 $len=3
866 | reuse #refresh_idpg
867 | send.modbus $dev=2 $reg=6 $len=2 //RCU2
868 | send.modbus $dev=3 $reg=6 $len=2 //RCU3
869 | //send.modbus $dev=4 $reg=6 $len=2 //RCU4
870 | reuse #dnd_relay
871 | exit
872
873
874
875
876
877
878
879 | function top_inputs_on
880 | if bit true #pir1_close $bit=25 //input 9 on
881 | if bit true #pir2_close $bit=26 //input 10 on
882 | if bit true #pir3_close $bit=27 //input 11 on
883 | if bit true #pir4_close $bit=28 //input 12 on
884 | if bit true #pir5_close $bit=29 //input 13 on
885 | if bit true #pir6_close $bit=30 //input 14 on
886 | if bit true #pir1_close $bit=31 //input 15 on
887 | if bit true #pir2_close $bit=32 //input 16 on
888 | exit
889
890
891
892 | function top_inputs_off
893 | if bit true #pir1_open $bit=25 //input 9 off
894 | if bit true #pir2_open $bit=26 //input 10 off
895 | if bit true #pir3_open $bit=27 //input 11 off
896 | if bit true #pir4_open $bit=28 //input 12 off
897 | if bit true #pir5_open $bit=29 //input 13 off
898 | if bit true #pir6_open $bit=30 //input 14 off
899 | if bit true #pir1_open $bit=31 //input 15 off
900 | if bit true #pir2_open $bit=32 //input 16 off
901 | exit
902
903
904
905
906 | //modbus receive
907
908 | function receive_rcu2_workflow | ok
909 | save $var=workflow
910 | send.modbus $dev=server $reg=4 $len=3
911 | send.modbus $dev=3 $reg=6 $len=2 //send rcu3
912 | reuse #refresh_idpg
913 | reuse #dnd_relay
914 | exit
915
916
917 | function receive_rcu3_workflow | ok
918 | save $var=workflow
919 | send.modbus $dev=server $reg=4 $len=3
920 | send.modbus $dev=2 $reg=6 $len=2 //send rcu2
921 | reuse #refresh_idpg
922 | reuse #dnd_relay
923 | exit
924
925
926 | function receive_rcu2_notifications
927 | if equal #rcu2_restart $dec=0
928 | exit
929
930
931 | function rcu2_restart
932 | send.modbus $dev=server $reg=0 $hex=1 //RCU2 startup
933 | exit
934
935
936
937 | function receive_rcu2_relays | ok
938 | save $var=rcu2_relays
939 | exit
940
941 | function receive_rcu3_relays | ok
942 | save $var=rcu3_relays
943 | exit
944
945 | //function receive_rcu4_relays | ok
946 | //save $var=rcu4_relays
947 | //exit
948
949
950
951
952 | function receive_rcu2_bed1_panel | ok
953 | if equal #bed1_on/off $dec=1
954 | if equal #bed1_relax $dec=2
955 | if equal #bed1_night $dec=3
956 | exit
957
958
959 | function receive_rcu3_bed1_panel | ok
960 | if equal #bed1_relax $dec=1
961 | if equal #bed1_light $dec=2
962 | exit
963
964
965 | function receive_rcu2_bed2_panel | ok
966 | if equal #bed2_on/off $dec=1
967 | if equal #bed2_relax $dec=2
968 | if equal #bed2_night $dec=3
969 | if equal #bed2_light $dec=4
970 | exit
971
972
973 | function receive_rcu2_bed3_panel | ok
974 | if equal #bed3_on/off $dec=1
975 | if equal #bed3_relax $dec=2
976 | if equal #bed3_night $dec=3
977 | if equal #bed3_light $dec=4
978 | exit
979
980
981
982 | function receive_rcu2_master_bed_panel | ok
983 | if equal #master_bed_relax $dec=1
984 | if equal #master_bed_light $dec=2
985 | exit
986
987
988
989 | function receive_rcu3_notifications
990 | if equal #rcu3_restart $dec=0
991 | exit
992
993
994 | function rcu3_restart
995 | send.modbus $dev=server $reg=0 $hex=2 //RCU3 startup
996 | exit
997
998
999
1000
1001 | function receive_rcu3_master_bed_panel | ok
1002 | if equal #master_bed_on/off $dec=1
1003 | if equal #master_bed_relax $dec=2
1004 | if equal #master_bed_night $dec=3
1005 | if equal #master_bed_light $dec=4
1006 | exit
1007
1008
1009 | function receive_rcu3_bath1_panel | ok
1010 | if equal #bath1_relax $dec=1
1011 | if equal #bath1_master $dec=2
1012 | if equal #bath1_night $dec=3
1013 | exit
1014
1015
1016 | function receive_rcu2_bath2_panel | ok
1017 | if equal #bath2_relax $dec=1
1018 | if equal #bath2_master $dec=2
1019 | if equal #bath2_night $dec=3
1020 | exit
1021
1022
1023 | function receive_rcu2_bath3_panel | ok
1024 | if equal #bath3_relax $dec=1
1025 | if equal #bath3_master $dec=2
1026 | if equal #bath3_night $dec=3
1027 | exit
1028
1029
1030 | function receive_rcu2_master_bath_panel | ok
1031 | if equal #master_bath_relax $dec=1
1032 | if equal #master_bath_master $dec=2
1033 | if equal #master_bath_night $dec=3
1034 | exit
1035
1036
1037
1038 | function receive_rcu3_entrance_panel | ok
1039 | if equal #entrance_master $dec=1
1040 | if equal #entrance_relax $dec=2
1041 | if equal #living_room $dec=3
1042 | if equal #lounge_light $dec=4
1043 | if equal #kitchen_light $dec=5
1044 | if equal #dining_light $dec=6
1045 | exit
1046
1047
1048
1049 | function receive_rcu3_corridor_panel | ok
1050 | if equal #corridor_light $dec=1
1051 | if equal #living_room $dec=2
1052 | if equal #storage1_light $dec=3
1053 | if equal #storage2_light $dec=4
1054 | exit
1055
1056
1057
1058 | function receive_rcu3_motion
1059 | if equal #pir6_close $dec=1
1060 | goto #pir6_open
1061
1062
1063 | function receive_rcu4_notifications
1064 | if equal #rcu4_restart $dec=0
1065 | exit
1066
1067
1068 | function rcu4_restart
1069 | send.modbus $dev=server $reg=0 $hex=3 //RCU4 startup
1070 | exit
1071
1072
1073
1074
1075 | function receive_rcu4_fcu_speed //7th FCU | ok
1076 | send.modbus $dev=server $reg=13 $len=4
1077 | exit
1078
1079
1080
1081 | function receive_rcu4_fcu_setpoint | ok
1082 | load shift $hex=6 //7th FCU
1083 | send.modbus $dev=server $reg=11 $len=8
1084 | exit
1085
1086
1087 | function receive_rcu4_fcu_current_temp | ok
1088 | load shift $hex=6 //7th FCU
1089 | send.modbus $dev=server $reg=10 $len=8
1090 | exit
1091
1092
1093 | function receive_rcu4_PT100_7_water_return | ok
1094 | load shift $hex=71
1095 | send.modbus $dev=server $reg=255 $len=16
1096 | exit
1097
1098
1099 | function receive_rcu4_PT100_7_water_supply | ok
1100 | load shift $hex=72
1101 | send.modbus $dev=server $reg=255 $len=16
1102 | exit
1103
1104
1105 | function receive_rcu4_PT100_7_air_return | ok
1106 | load shift $hex=73
1107 | send.modbus $dev=server $reg=255 $len=16
1108 | exit
1109
1110
1111 | function receive_rcu4_PT100_7_air_supply | ok
1112 | load shift $hex=74
1113 | send.modbus $dev=server $reg=255 $len=16
1114 | exit
1115
1116
1117
1118
1119
1120
1121 | //modbus send
1122
1123
1124 | function maids_bathroom | ok
1125 | rcu3_relays.xor $relay=16
1126 | send.modbus $dev=3 $reg=7 $len=2
1127 | exit
1128
1129
1130 | function maids_bedroom | ok
1131 | rcu3_relays.xor $relay=15
1132 | send.modbus $dev=3 $reg=7 $len=2
1133 | exit
1134
1135
1136
1137
1138 | function powder_room | ok
1139 | load $var=rcu4_relays
1140 | if bit true #powder_room_off $relay=6,7
1141 | rcu4_relays.or $relay=6,7
1142 | send.modbus $dev=4 $reg=7 $len=2
1143 | exit
1144 | function powder_room_off
1145 | rcu4_relays.and $relay=6,7
1146 | send.modbus $dev=4 $reg=7 $len=2
1147 | exit
1148
1149
1150
1151
1152 | function bed1_on/off | ok
1153 | load $var=rcu4_relays
1154 | math.and $relay=1-8,15-32
1155 | if not equal #bed1_on $relay=9-14
1156 | rcu4_relays.and $relay=9-14
1157 | send.modbus $dev=4 $reg=7 $len=2
1158 | exit
1159 | function bed1_on
1160 | rcu4_relays.or $relay=9-14
1161 | send.modbus $dev=4 $reg=7 $len=2
1162 | exit
1163
1164
1165
1166 | function bed1_relax | ok
1167 | load $var=rcu4_relays
1168 | math.and $relay=1-8,11-32
1169 | if not equal #bed1_relax_on $relay=10
1170 | rcu4_relays.and $relay=9,10
1171 | send.modbus $dev=4 $reg=7 $len=2
1172 | exit
1173 | function bed1_relax_on
1174 | rcu4_relays.or.and $relay=10 $relay=9
1175 | send.modbus $dev=4 $reg=7 $len=2
1176 | exit
1177
1178
1179
1180 | function bed1_night | ok
1181 | load $var=rcu4_relays
1182 | if bit true #bed1_night_off $relay=10,14
1183 | rcu4_relays.or $relay=10,14
1184 | send.modbus $dev=4 $reg=7 $len=2
1185 | exit
1186 | function bed1_night_off
1187 | rcu4_relays.and $relay=10,14
1188 | send.modbus $dev=4 $reg=7 $len=2
1189 | exit
1190
1191
1192 | function bed1_light | ok
1193 | rcu4_relays.xor $relay=9
1194 | send.modbus $dev=4 $reg=7 $len=2
1195 | exit
1196
1197
1198
1199
1200 | function bed2_on/off | ok
1201 | load $var=rcu3_relays
1202 | math.and $relay=1-6,8,15-32
1203 | if not equal #bed2_on $relay=7,9-14
1204 | rcu3_relays.and $relay=7,9-14
1205 | send.modbus $dev=3 $reg=7 $len=2
1206 | exit
1207 | function bed2_on
1208 | rcu3_relays.or $relay=7,9-14
1209 | send.modbus $dev=3 $reg=7 $len=2
1210 | exit
1211
1212
1213 | function bed2_relax | ok
1214 | load $var=rcu3_relays
1215 | math.and $relay=1-6,8,10-32
1216 | if not equal #bed2_relax_on $relay=9
1217 | rcu3_relays.and $relay=7,9
1218 | send.modbus $dev=3 $reg=7 $len=2
1219 | exit
1220 | function bed2_relax_on
1221 | rcu3_relays.or.and $relay=9 $relay=7
1222 | send.modbus $dev=3 $reg=7 $len=2
1223 | exit
1224
1225
1226 | function bed2_night | ok
1227 | load $var=rcu3_relays
1228 | if bit true #bed2_night_off $relay=9,14
1229 | rcu3_relays.or $relay=9,14
1230 | send.modbus $dev=3 $reg=7 $len=2
1231 | exit
1232 | function bed2_night_off
1233 | rcu3_relays.and $relay=9,14
1234 | send.modbus $dev=3 $reg=7 $len=2
1235 | exit
1236
1237
1238
1239 | function bed2_light | ok
1240 | rcu3_relays.xor $relay=7
1241 | send.modbus $dev=3 $reg=7 $len=2
1242 | exit
1243
1244
1245
1246 | function bed3_on/off | ok
1247 | load $var=rcu2_relays
1248 | math.and $relay=1-10,12-32
1249 | if not equal #bed3_on $relay=11
1250 | load $var=rcu3_relays
1251 | math.and $relay=7-32
1252 | if not equal #bed3_on $relay=1-6
1253 | rcu2_relays.and $relay=11
1254 | send.modbus $dev=2 $reg=7 $len=2
1255 | rcu3_relays.and $relay=1-6
1256 | send.modbus $dev=3 $reg=7 $len=2
1257 | exit
1258 | function bed3_on
1259 | rcu2_relays.or $relay=11
1260 | send.modbus $dev=2 $reg=7 $len=2
1261 | rcu3_relays.or $relay=1-6
1262 | send.modbus $dev=3 $reg=7 $len=2
1263 | exit
1264
1265
1266
1267 | function bed3_relax | ok
1268 | load $var=rcu3_relays
1269 | math.and $relay=3-32
1270 | if not equal #bed3_relax_on $relay=2
1271 | rcu3_relays.and $relay=1,2
1272 | send.modbus $dev=3 $reg=7 $len=2
1273 | exit
1274 | function bed3_relax_on
1275 | rcu3_relays.or.and $relay=2 $relay=1
1276 | send.modbus $dev=3 $reg=7 $len=2
1277 | exit
1278
1279
1280
1281
1282 | function bed3_night | ok
1283 | load $var=rcu3_relays
1284 | if bit true #bed3_night_off $relay=2,6
1285 | rcu3_relays.or $relay=2,6
1286 | send.modbus $dev=3 $reg=7 $len=2
1287 | exit
1288 | function bed3_night_off
1289 | rcu3_relays.and $relay=2,6
1290 | send.modbus $dev=3 $reg=7 $len=2
1291 | exit
1292
1293
1294
1295 | function bed3_light | ok
1296 | rcu3_relays.xor $relay=1
1297 | send.modbus $dev=3 $reg=7 $len=2
1298 | exit
1299
1300
1301
1302
1303
1304 | function master_bed_on/off | ok
1305 | load $var=rcu2_relays
1306 | math.and $relay=2-4,10-32
1307 | if not equal #master_bed_on $relay=1,5-9
1308 | rcu2_relays.and $relay=1,5-9
1309 | send.modbus $dev=2 $reg=7 $len=2
1310 | exit
1311 | function master_bed_on
1312 | rcu2_relays.or $relay=1,5-9
1313 | send.modbus $dev=2 $reg=7 $len=2
1314 | exit
1315
1316
1317
1318 | function master_bed_relax | ok
1319 | load $var=rcu2_relays
1320 | math.and $relay=2-8,10-32
1321 | if not equal #master_bed_relax_on $relay=1
1322 | rcu2_relays.and $relay=1,9
1323 | send.modbus $dev=2 $reg=7 $len=2
1324 | exit
1325 | function master_bed_relax_on
1326 | rcu2_relays.or.and $relay=1 $relay=9
1327 | send.modbus $dev=2 $reg=7 $len=2
1328 | exit
1329
1330
1331
1332
1333 | function master_bed_night | ok
1334 | load $var=rcu2_relays
1335 | if bit true #master_bed_night_off $relay=1,8
1336 | rcu2_relays.or $relay=1,8
1337 | send.modbus $dev=2 $reg=7 $len=2
1338 | exit
1339 | function master_bed_night_off
1340 | rcu2_relays.and $relay=1,8
1341 | send.modbus $dev=2 $reg=7 $len=2
1342 | exit
1343
1344
1345
1346 | function master_bed_light | ok
1347 | rcu2_relays.xor $relay=9
1348 | send.modbus $dev=2 $reg=7 $len=2
1349 | exit
1350
1351
1352
1353 | function bath1_relax | ok
1354 | load $var=rcu4_relays
1355 | math.and $relay=1-10,15-32
1356 | if not equal #bath1_relax_on $relay=11
1357 | rcu4_relays.and $relay=11-14
1358 | send.modbus $dev=4 $reg=7 $len=2
1359 | exit
1360 | function bath1_relax_on
1361 | rcu4_relays.or.and $relay=11 $relay=12-14
1362 | send.modbus $dev=4 $reg=7 $len=2
1363 | exit
1364
1365
1366
1367 | function bath1_master | ok
1368 | load $var=rcu4_relays
1369 | if bit true #bath1_master_off $relay=11-13
1370 | rcu4_relays.or $relay=11-13
1371 | send.modbus $dev=4 $reg=7 $len=2
1372 | exit
1373 | function bath1_master_off
1374 | rcu4_relays.and $relay=11-13
1375 | send.modbus $dev=4 $reg=7 $len=2
1376 | exit
1377
1378
1379
1380 | function bath1_night | ok
1381 | rcu4_relays.xor $relay=14
1382 | send.modbus $dev=4 $reg=7 $len=2
1383 | exit
1384
1385
1386
1387
1388
1389 | function bath2_relax | ok
1390 | load $var=rcu3_relays
1391 | math.and $relay=1-9,15-32
1392 | if not equal #bath2_relax_on $relay=10
1393 | rcu3_relays.and $relay=10-14
1394 | send.modbus $dev=3 $reg=7 $len=2
1395 | exit
1396 | function bath2_relax_on
1397 | rcu3_relays.or.and $relay=10 $relay=11-14
1398 | send.modbus $dev=3 $reg=7 $len=2
1399 | exit
1400
1401
1402 | function bath2_master | ok
1403 | load $var=rcu3_relays
1404 | if bit true #bath2_master_off $relay=10-13
1405 | rcu3_relays.or $relay=10-13
1406 | send.modbus $dev=3 $reg=7 $len=2
1407 | exit
1408 | function bath2_master_off
1409 | rcu3_relays.and $relay=10-13
1410 | send.modbus $dev=3 $reg=7 $len=2
1411 | exit
1412
1413 | function bath2_night | ok
1414 | rcu3_relays.xor $relay=14
1415 | send.modbus $dev=3 $reg=7 $len=2
1416 | exit
1417
1418
1419
1420
1421
1422 | function bath3_relax | ok
1423 | load $var=rcu2_relays
1424 | math.and $relay=1-10,12-32
1425 | if not equal #bath3_relax_on $hex=0
1426 | load $var=rcu3_relays
1427 | math.and $relay=1,2,7-32
1428 | if not equal #bath3_relax_on $relay=3
1429 | rcu2_relays.and $relay=11
1430 | send.modbus $dev=2 $reg=7 $len=2
1431 | rcu3_relays.and $relay=3-6
1432 | send.modbus $dev=3 $reg=7 $len=2
1433 | exit
1434 | function bath3_relax_on
1435 | rcu2_relays.and $relay=11
1436 | send.modbus $dev=2 $reg=7 $len=2
1437 | rcu3_relays.or.and $relay=3 $relay=4-6
1438 | send.modbus $dev=3 $reg=7 $len=2
1439 | exit
1440
1441
1442 | function bath3_master | ok
1443 | load $var=rcu2_relays
1444 | if bit true #bath3_master_off $relay=11
1445 | load $var=rcu3_relays
1446 | if bit true #bath3_master_off $relay=3-5
1447 | rcu2_relays.or $relay=11
1448 | send.modbus $dev=2 $reg=7 $len=2
1449 | rcu3_relays.or $relay=3-5
1450 | send.modbus $dev=3 $reg=7 $len=2
1451 | exit
1452 | function bath3_master_off
1453 | rcu2_relays.and $relay=11
1454 | send.modbus $dev=2 $reg=7 $len=2
1455 | rcu3_relays.and $relay=3-5
1456 | send.modbus $dev=3 $reg=7 $len=2
1457 | exit
1458
1459 | function bath3_night | ok
1460 | rcu3_relays.xor $relay=6
1461 | send.modbus $dev=3 $reg=7 $len=2
1462 | exit
1463
1464
1465
1466
1467
1468 | function master_bath_relax | ok
1469 | load $var=rcu2_relays
1470 | math.and $relay=1-4,9-32
1471 | if not equal #master_bath_relax_on $relay=5
1472 | rcu2_relays.and $relay=5-8
1473 | send.modbus $dev=2 $reg=7 $len=2
1474 | exit
1475 | function master_bath_relax_on
1476 | rcu2_relays.or.and $relay=5 $relay=6-8
1477 | send.modbus $dev=2 $reg=7 $len=2
1478 | exit
1479
1480
1481 | function master_bath_master | ok
1482 | load $var=rcu2_relays
1483 | if bit true #master_bath_master_off $relay=5-7
1484 | rcu2_relays.or $relay=5-7
1485 | send.modbus $dev=2 $reg=7 $len=2
1486 | exit
1487 | function master_bath_master_off
1488 | rcu2_relays.and $relay=5-7
1489 | send.modbus $dev=2 $reg=7 $len=2
1490 | exit
1491
1492 | function master_bath_night | ok
1493 | rcu2_relays.xor $relay=8
1494 | send.modbus $dev=2 $reg=7 $len=2
1495 | exit
1496
1497
1498
1499
1500
1501
1502
1503 | function entrance_master | ok
1504 | load $var=rcu2_relays
1505 | math.and $relay=1-12,15-32
1506 | if not equal #entrance_master_on $relay=13,14
1507 | load $var=rcu4_relays
1508 | math.and $relay=1-3,6-14,17-32
1509 | if not equal #entrance_master_on $relay=4,5,15,16
1510 | rcu2_relays.and $relay=13,14
1511 | send.modbus $dev=2 $reg=7 $len=2
1512 | rcu4_relays.and $relay=4,5,15,16
1513 | send.modbus $dev=4 $reg=7 $len=2
1514 | exit
1515 | function entrance_master_on
1516 | rcu2_relays.or $relay=13,14
1517 | send.modbus $dev=2 $reg=7 $len=2
1518 | rcu4_relays.or $relay=4,5,15,16
1519 | send.modbus $dev=4 $reg=7 $len=2
1520 | exit
1521
1522
1523
1524 | function entrance_relax | ok
1525 | load $var=rcu2_relays
1526 | math.and $relay=1-12,14-32
1527 | if not equal #entrance_relax_on $relay=13
1528 | load $var=rcu4_relays
1529 | math.and $relay=1-3,6-14,17-32
1530 | if not equal #entrance_relax_on $relay=16
1531 | rcu2_relays.and $relay=13
1532 | send.modbus $dev=2 $reg=7 $len=2
1533 | rcu4_relays.and $relay=4,5,15,16
1534 | send.modbus $dev=4 $reg=7 $len=2
1535 | exit
1536 | function entrance_relax_on
1537 | rcu2_relays.or $relay=13
1538 | send.modbus $dev=2 $reg=7 $len=2
1539 | rcu4_relays.or.and $relay=16 $relay=4,5,15
1540 | send.modbus $dev=4 $reg=7 $len=2
1541 | exit
1542
1543
1544
1545
1546
1547 | function living_room | ok
1548 | load $var=rcu2_relays
1549 | math.and $relay=1-12,15-32
1550 | if not equal #living_room_on $relay=13,14
1551 | load $var=rcu4_relays
1552 | math.and $relay=1-3,5-14,17-32
1553 | if not equal #living_room_on $relay=4,15,16
1554 | rcu2_relays.and $relay=13,14
1555 | send.modbus $dev=2 $reg=7 $len=2
1556 | rcu4_relays.and $relay=4,15,16
1557 | send.modbus $dev=4 $reg=7 $len=2
1558 | exit
1559 | function living_room_on
1560 | rcu2_relays.or $relay=13,14
1561 | send.modbus $dev=2 $reg=7 $len=2
1562 | rcu4_relays.or $relay=4,15,16
1563 | send.modbus $dev=4 $reg=7 $len=2
1564 | exit
1565
1566
1567
1568 | function lounge_light | ok
1569 | rcu4_relays.xor $relay=15
1570 | send.modbus $dev=4 $reg=7 $len=2
1571 | exit
1572
1573
1574
1575 | function kitchen_light | ok
1576 | rcu4_relays.xor $relay=5
1577 | send.modbus $dev=4 $reg=7 $len=2
1578 | exit
1579
1580
1581
1582
1583
1584 | function dining_light | ok
1585 | rcu4_relays.xor $relay=16
1586 | send.modbus $dev=4 $reg=7 $len=2
1587 | exit
1588
1589
1590
1591
1592
1593 | function corridor_light | ok
1594 | rcu2_relays.xor $relay=4
1595 | send.modbus $dev=2 $reg=7 $len=2
1596 | exit
1597
1598
1599
1600 | function storage1_light | ok
1601 | rcu2_relays.xor $relay=2
1602 | send.modbus $dev=2 $reg=7 $len=2
1603 | exit
1604
1605
1606 | function storage2_light | ok
1607 | rcu2_relays.xor $relay=3
1608 | send.modbus $dev=2 $reg=7 $len=2
1609 | exit
1610
1611
1612
1613
1614
1615
1616
1617
1618 | // gsw area
1619
1620
1621
1622 | function GSW02A_refresh | ok
1623 | load $dec=0
1624 | send.modbus $dev=FE $reg=13 $len=4
1625 | exit
1626 | function GSW02A_btn_4
1627 | reuse #maids_bathroom
1628 | load $hex=400
1629 | function GSW02A_btn_common
1630 | send.modbus $dev=FE $reg=13 $len=4
1631 | wait $sec=0.15
1632 | load $hex=440
1633 | send.modbus $dev=FE $reg=13 $len=4
1634 | reuse #GSW02A_refresh $sec=15
1635 | load $hex=1 // cause and interrupt for GS
1636 | goto #set_last_action
1637 | function GSW02A_btn_6
1638 | reuse #maids_bedroom
1639 | load $hex=40
1640 | goto #GSW02A_btn_common
1641
1642
1643
1644
1645 | function GSW01_refresh | ok
1646 | load $dec=0
1647 | send.modbus $dev=FE $reg=13 $len=4
1648 | exit
1649 | function GSW01_btn_5
1650 | reuse #powder_room
1651 | load $hex=0
1652 | function GSW01_btn_common
1653 | send.modbus $dev=FE $reg=13 $len=4
1654 | wait $sec=0.15
1655 | load $hex=100
1656 | send.modbus $dev=FE $reg=13 $len=4
1657 | reuse #GSW01_refresh $sec=15
1658 | load $hex=1 // cause and interrupt for GS
1659 | goto #set_last_action
1660
1661
1662
1663
1664 | function dnd_relay | ok
1665 | load $var=workflow
1666 | if equal #+3 $hex=7
1667 | rcu.unset $relay=13
1668 | exit
1669 | rcu.set $relay=13
1670 | exit
1671
1672
1673
1674
1675
1676
1677
1678
1679 | //motion functions
1680
1681 | function pir1_close
1682 | pir.or $relay=1
1683 | reuse #motion_relays $sec=2
1684 | load $hex=2 // cause & interrupt pir1
1685 | goto #set_last_action
1686
1687
1688 | function pir2_close
1689 | pir.or $relay=2
1690 | reuse #motion_relays $sec=2
1691 | load $hex=3 // cause & interrupt pir2
1692 | goto #set_last_action
1693
1694 | function pir3_close
1695 | pir.or $relay=3
1696 | reuse #motion_relays $sec=2
1697 | load $hex=4 // cause & interrupt pir3
1698 | goto #set_last_action
1699
1700
1701 | function pir4_close
1702 | pir.or $relay=4
1703 | reuse #motion_relays $sec=2
1704 | load $hex=5 // cause & interrupt pir4
1705 | goto #set_last_action
1706
1707
1708 | function pir5_close
1709 | pir.or $relay=5
1710 | reuse #motion_relays $sec=2
1711 | load $hex=6 // cause & interrupt pir5
1712 | goto #set_last_action
1713
1714
1715 | function pir6_close
1716 | pir.or $relay=6
1717 | reuse #motion_relays $sec=2
1718 | load $hex=7 // cause & interrupt pir6
1719 | goto #set_last_action
1720
1721
1722
1723
1724 | function motion_relays
1725 | load $var=rcu2_relays
1726 | if bit true #+5 $relay=10,15,16
1727 | rcu2_relays.or $bit=10,15,16
1728 | send.modbus $dev=2 $reg=7 $len=2
1729 | load $var=rcu3_relays
1730 | if bit true #exit $relay=8
1731 | rcu3_relays.or $bit=8
1732 | send.modbus $dev=3 $reg=7 $len=2
1733 | exit
1734
1735
1736
1737
1738 | function pir1_open
1739 | pir.and $relay=1
1740 | reuse #check_exit_scene $sec=20 $dev=tag1
1741 | exit
1742
1743
1744 | function pir2_open
1745 | pir.and $relay=2
1746 | reuse #check_exit_scene $sec=20 $dev=tag1
1747 | exit
1748
1749
1750 | function pir3_open
1751 | pir.and $relay=3
1752 | reuse #check_exit_scene $sec=20 $dev=tag1
1753 | exit
1754
1755
1756 | function pir4_open
1757 | pir.and $relay=4
1758 | reuse #check_exit_scene $sec=20 $dev=tag1
1759 | exit
1760
1761
1762 | function pir5_open
1763 | pir.and $relay=5
1764 | reuse #check_exit_scene $sec=20 $dev=tag1
1765 | exit
1766
1767
1768 | function pir6_open
1769 | pir.and $relay=6
1770 | reuse #check_exit_scene $sec=20 $dev=tag1
1771 | exit
1772
1773
1774
1775 | function check_exit_scene
1776 | load $var=last_action
1777 | if bit true #exit $hex=ff
1778 | load $var=pir
1779 | if bit true #exit $relay=1-6
1780 | load $var=user
1781 | if equal #+3 $hex=10 // if with staff
1782 | reuse #master_off_check $min=120
1783 | exit
1784 | reuse #master_off_check $min=5
1785 | exit
1786
1787
1788
1789
1790 | function master_off_check
1791 | load $var=pir
1792 | if bit true #exit $relay=1-6
1793 | load $var=last_action
1794 | if bit true #exit $hex=ff
1795 | load $var=user
1796 | if equal #exit $dec=0
1797 | send.modbus $dev=2 $reg=7 $len=2 $relay=15,16 //unset rcu2 relays
1798 | send.modbus $dev=3 $reg=7 $len=2 $hex=0 //unset rcu3 relays
1799 | send.modbus $dev=4 $reg=7 $len=2 $hex=0 //unset rcu4 relays
1800 | user.unset
1801 | send.modbus $dev=2 $reg=5 $len=2 //rcu2 user
1802 | send.modbus $dev=3 $reg=5 $len=2 //rcu3 user
1803 | send.modbus $dev=4 $reg=5 $len=2 //rcu4 user
1804 | send.modbus $dev=server $reg=3 $len=16 //User absence
1805 | season.set $hex=01 //summer - min fan speed
1806 | function tag_conditional_check_without_user
1807 | reuse #refresh_tag2 $dev=tag2
1808 | load $var=room_empty
1809 | if less than #+3 $hex=8000
1810 | math.and $relay=16
1811 | math.add $var=temp2
1812 | send.modbus $dev=tag2 $reg=25 $len=2
1813 | reuse #refresh_tag3 $dev=tag3
1814 | load $var=room_empty
1815 | if less than #+3 $hex=8000
1816 | math.and $relay=16
1817 | math.add $var=temp3
1818 | send.modbus $dev=tag3 $reg=25 $len=2
1819 | reuse #refresh_tag4 $dev=tag4
1820 | load $var=room_empty
1821 | if less than #+3 $hex=8000
1822 | math.and $relay=16
1823 | math.add $var=temp4
1824 | send.modbus $dev=tag4 $reg=25 $len=2
1825 | reuse #refresh_tag5 $dev=tag5
1826 | load $var=room_empty
1827 | if less than #+3 $hex=8000
1828 | math.and $relay=16
1829 | math.add $var=temp5
1830 | send.modbus $dev=tag5 $reg=25 $len=2
1831 | wait $sec=2
1832 | load $hex=80
1833 | send.modbus $dev=tag2 $reg=13 $len=4
1834 | send.modbus $dev=tag3 $reg=13 $len=4
1835 | send.modbus $dev=tag4 $reg=13 $len=4
1836 | send.modbus $dev=tag5 $reg=13 $len=4
1837 | function wc_tag_refresh_without_user
1838 | rcu.read input
1839 | math.xor $bit=2
1840 | if bit true #exit $bit=2
1841 | reuse #refresh_tag1 $dev=tag1
1842 | load $var=room_empty
1843 | if less than #+3 $hex=8000
1844 | math.and $relay=16
1845 | math.add $var=temp1
1846 | send.modbus $dev=tag1 $reg=25 $len=2
1847 | reuse #refresh_tag6 $dev=tag6
1848 | load $var=room_empty
1849 | if less than #+3 $hex=8000
1850 | math.and $relay=16
1851 | math.add $var=temp6
1852 | send.modbus $dev=tag6 $reg=25 $len=2
1853 | wait $sec=2
1854 | load $hex=80
1855 | send.modbus $dev=tag1 $reg=13 $len=4
1856 | send.modbus $dev=tag6 $reg=13 $len=4
1857 | exit
1858
1859
1860
1861
1862
1863 | function set_last_action
1864 | math.mul.or $hex=100 $var=last_action
1865 | save $var=last_action
1866 | math.and $hex=ff
1867 | if not equal #skip_notify_interrupt $hex=0
1868 | load $var=user
1869 | if equal #skip_notify_interrupt $hex=0 // if guest 0 this is not an interrupt
1870 | load $var=last_action
1871 | math.div $hex=100
1872 | if equal #skip_notify_interrupt $hex=0
1873 | send.modbus $dev=server $reg=17 $len=16 // interrupt
1874 | function skip_notify_interrupt
1875 | last_action.div $hex=100
1876 | load $var=user
1877 | if bit true #exit $hex=ff
1878 | goto #motion_detect_from_inside
1879 | exit
1880
1881
1882
1883
1884 | function motion_detect_from_inside
1885 | user.set $var=temp_user
1886 | send.modbus $dev=2 $reg=5 $len=2 //rcu2 user
1887 | wait $sec=0.15
1888 | send.modbus $dev=3 $reg=5 $len=2 //rcu3 user
1889 | wait $sec=0.15
1890 | send.modbus $dev=4 $reg=5 $len=2 //rcu4 user
1891 | load $var=last_action // cause of user presence
1892 | send.modbus $dev=server $reg=2 $len=16
1893 | season.set $hex=11 //summer + min fan speed
1894 | send.modbus $dev=2 $reg=7 $len=2 $var=rcu2_relays //rcu2 relays
1895 | send.modbus $dev=3 $reg=7 $len=2 $var=rcu3_relays //rcu3 relays
1896 | send.modbus $dev=4 $reg=7 $len=2 $var=rcu4_relays //rcu4 relays
1897 | goto #tag_conditional_check_with_user
1898 | exit
1899
1900
1901
1902
1903 | function power_recover
1904 | send.modbus $dev=2 $reg=7 $len=2 $var=rcu2_relays // rcu2 relays
1905 | send.modbus $dev=3 $reg=7 $len=2 $var=rcu3_relays //rcu3 relays
1906 | send.modbus $dev=4 $reg=7 $len=2 $var=rcu4_relays //rcu4 relays
1907 | reuse #dnd_relay
1908 | exit
1909
1910
1911 | //tempearture probe
1912
1913
1914
1915 | function temp_probe_cycle
1916 | //first hub
1917 | read.modbus $dev=13 $reg=3
1918 | if equal goto #+4 $var=PT100_1_water_return
1919 | save $var=PT100_1_water_return
1920 | load shift $hex=11
1921 | send.modbus $dev=server $reg=255 $len=16
1922 | wait $sec=30
1923 | read.modbus $dev=13 $reg=4
1924 | if equal goto #+4 $var=PT100_1_water_supply
1925 | save $var=PT100_1_water_supply
1926 | load shift $hex=12
1927 | send.modbus $dev=server $reg=255 $len=16
1928 | wait $sec=30
1929 | read.modbus $dev=13 $reg=5
1930 | if equal goto #+4 $var=PT100_1_air_return
1931 | save $var=PT100_1_air_return
1932 | load shift $hex=13
1933 | send.modbus $dev=server $reg=255 $len=16
1934 | wait $sec=30
1935 | read.modbus $dev=13 $reg=6
1936 | if equal goto #+4 $var=PT100_1_air_supply
1937 | save $var=PT100_1_air_supply
1938 | load shift $hex=14
1939 | send.modbus $dev=server $reg=255 $len=16
1940 | wait $sec=30
1941 | //second hub
1942 | read.modbus $dev=14 $reg=3
1943 | if equal goto #+4 $var=PT100_2_water_return
1944 | save $var=PT100_2_water_return
1945 | load shift $hex=21
1946 | send.modbus $dev=server $reg=255 $len=16
1947 | wait $sec=30
1948 | read.modbus $dev=14 $reg=4
1949 | if equal goto #+4 $var=PT100_2_water_supply
1950 | save $var=PT100_2_water_supply
1951 | load shift $hex=22
1952 | send.modbus $dev=server $reg=255 $len=16
1953 | wait $sec=30
1954 | read.modbus $dev=14 $reg=5
1955 | if equal goto #+4 $var=PT100_2_air_return
1956 | save $var=PT100_2_air_return
1957 | load shift $hex=23
1958 | send.modbus $dev=server $reg=255 $len=16
1959 | wait $sec=30
1960 | read.modbus $dev=14 $reg=6
1961 | if equal goto #+4 $var=PT100_2_air_supply
1962 | save $var=PT100_2_air_supply
1963 | load shift $hex=24
1964 | send.modbus $dev=server $reg=255 $len=16
1965 | wait $sec=30
1966 | //third hub
1967 | read.modbus $dev=15 $reg=3
1968 | if equal goto #+4 $var=PT100_3_water_return
1969 | save $var=PT100_3_water_return
1970 | load shift $hex=31
1971 | send.modbus $dev=server $reg=255 $len=16
1972 | wait $sec=30
1973 | read.modbus $dev=15 $reg=4
1974 | if equal goto #+4 $var=PT100_3_water_supply
1975 | save $var=PT100_3_water_supply
1976 | load shift $hex=32
1977 | send.modbus $dev=server $reg=255 $len=16
1978 | wait $sec=30
1979 | read.modbus $dev=15 $reg=5
1980 | if equal goto #+4 $var=PT100_3_air_return
1981 | save $var=PT100_3_air_return
1982 | load shift $hex=33
1983 | send.modbus $dev=server $reg=255 $len=16
1984 | wait $sec=30
1985 | read.modbus $dev=15 $reg=6
1986 | if equal goto #+4 $var=PT100_3_air_supply
1987 | save $var=PT100_3_air_supply
1988 | load shift $hex=34
1989 | send.modbus $dev=server $reg=255 $len=16
1990 | wait $sec=30
1991 | //fourth hub
1992 | read.modbus $dev=16 $reg=3
1993 | if equal goto #+4 $var=PT100_4_water_return
1994 | save $var=PT100_4_water_return
1995 | load shift $hex=41
1996 | send.modbus $dev=server $reg=255 $len=16
1997 | wait $sec=30
1998 | read.modbus $dev=16 $reg=4
1999 | if equal goto #+4 $var=PT100_4_water_supply
2000 | save $var=PT100_4_water_supply
2001 | load shift $hex=42
2002 | send.modbus $dev=server $reg=255 $len=16
2003 | wait $sec=30
2004 | read.modbus $dev=16 $reg=5
2005 | if equal goto #+4 $var=PT100_4_air_return
2006 | save $var=PT100_4_air_return
2007 | load shift $hex=43
2008 | send.modbus $dev=server $reg=255 $len=16
2009 | wait $sec=30
2010 | read.modbus $dev=16 $reg=6
2011 | if equal goto #+4 $var=PT100_4_air_supply
2012 | save $var=PT100_4_air_supply
2013 | load shift $hex=44
2014 | send.modbus $dev=server $reg=255 $len=16
2015 | wait $sec=30
2016 | //fifth hub
2017 | read.modbus $dev=17 $reg=3
2018 | if equal goto #+4 $var=PT100_5_water_return
2019 | save $var=PT100_5_water_return
2020 | load shift $hex=51
2021 | send.modbus $dev=server $reg=255 $len=16
2022 | wait $sec=30
2023 | read.modbus $dev=17 $reg=4
2024 | if equal goto #+4 $var=PT100_5_water_supply
2025 | save $var=PT100_5_water_supply
2026 | load shift $hex=52
2027 | send.modbus $dev=server $reg=255 $len=16
2028 | wait $sec=30
2029 | read.modbus $dev=17 $reg=5
2030 | if equal goto #+4 $var=PT100_5_air_return
2031 | save $var=PT100_5_air_return
2032 | load shift $hex=53
2033 | send.modbus $dev=server $reg=255 $len=16
2034 | wait $sec=30
2035 | read.modbus $dev=17 $reg=6
2036 | if equal goto #+4 $var=PT100_5_air_supply
2037 | save $var=PT100_5_air_supply
2038 | load shift $hex=54
2039 | send.modbus $dev=server $reg=255 $len=16
2040 | wait $sec=30
2041 | //sixth hub
2042 | read.modbus $dev=18 $reg=3
2043 | if equal goto #+4 $var=PT100_6_water_return
2044 | save $var=PT100_6_water_return
2045 | load shift $hex=61
2046 | send.modbus $dev=server $reg=255 $len=16
2047 | wait $sec=30
2048 | read.modbus $dev=18 $reg=4
2049 | if equal goto #+4 $var=PT100_6_water_supply
2050 | save $var=PT100_6_water_supply
2051 | load shift $hex=62
2052 | send.modbus $dev=server $reg=255 $len=16
2053 | wait $sec=30
2054 | read.modbus $dev=18 $reg=5
2055 | if equal goto #+4 $var=PT100_6_air_return
2056 | save $var=PT100_6_air_return
2057 | load shift $hex=63
2058 | send.modbus $dev=server $reg=255 $len=16
2059 | wait $sec=30
2060 | read.modbus $dev=18 $reg=6
2061 | if equal goto #+4 $var=PT100_6_air_supply
2062 | save $var=PT100_6_air_supply
2063 | load shift $hex=64
2064 | send.modbus $dev=server $reg=255 $len=16
2065 | goto #temp_probe_cycle $min=3
2066
2067
2068
2069
2070
2071
2072
2073
2074

## Program1
| ; |  | Dir: | C:\tini\ModularHotel\ABSlink\RCUmanager\bin\Release
| ;code |  | # | Description | done | Parameters (8 bytes)
0000 | 19 00 00 00 00 00 00 00; | #startup | 0x01 | GoTo & Wait | d | 0x01 | wait # tick |  | 2bytete optional goto |  |  | tick | [5 empty] | 00=nogoto 00=nowait
0001 | 00 00 00 00 09 2E ED 09; | version [35561452341814213551145390817034,9] |  |  | d | 0x03 | WaitTick/OrigDev |  | 2byte goto (acc->acc called) |  |  | tick | Relative, reuse of existing task with same device if present updating tick (used for timeout interactive mode) [multidev]
0002 | 01 01 28 00 00 00 00 00; | goto #debugging | 0x0a | Wait absolute | d | 1=value,3=1B,4=2B, 5=4B,a=acc[0]=RTC(add), |  |  |  |  | 2 byte empty |  |  |  | 4 byte value |  | 3-5= addr a-b uses RTC+acc[0]
0003 | 01 01 00 00 00 00 00 00; | reserved for ipad | 0x02 | Rcu Hardware | d | 0x01 | set relay |  | 0=accum, 1=value, 3=add1B, 4=add2B, 5=add4B | [5 empty] | byte low bitmap from relay 1 to 8
0004 | 01 01 00 00 00 00 00 00; | reserved for ipad |  |  | d | 0x02 | unset relay |  | 0=accum, 1=value, 3=add1B, 4=add2B, 5=add4B | [5 empty] | byte low bitmap from relay 1 to 8
0005 | 01 01 00 00 00 00 00 00; | reserved for ipad |  |  | d | 0x03 | read relays in accumulator
0006 | 01 01 00 00 00 00 00 00; | reserved for ipad |  |  | d | 0x04 | set all relays |  | 0=accum, 1=value, 3=add1B, 4=add2B, 5=add4B | [5 empty] | bitmap
0007 | 01 01 00 00 00 00 00 00; | reserved for ipad |  |  | d | 0x05 | set OUT Lock % |  | 0=accum, 1=value, 3=add1B, 4=add2B, 5=add4B | [5 empty] | 50% = 12Volt
0008 | 01 01 00 00 00 00 00 00; | reserved for ipad |  |  | d | 0x06 | set 0-10 V [1] |  | 0=accum, 1=value, 3=add1B, 4=add2B, 5=add4B
0009 | 01 01 00 00 00 00 00 00; | reserved for ipad |  |  | d | 0x07 | set 0-10 V [2] |  | 0=accum, 1=value, 3=add1B, 4=add2B, 5=add4B
000A | 01 01 00 00 00 00 00 00; | reserved for ipad |  |  |  | 0x08 | Input->Accumulator |  | Input # |  |  | Get inputs value in accumulator, if par1=0 all inputs (bitmap)
000B | 01 01 00 00 00 00 00 00; | reserved for ipad |  |  | d | 0x09 | set on relays |  | 0=accum, 1=value, 3=add1B, 4=add2B, 5=add4B | [5 empty] | bitmap
000C | 01 01 00 00 00 00 00 00; | reserved for ipad |  |  | d | 0x0a | set off relays |  | 0=accum, 1=value, 3=add1B, 4=add2B, 5=add4B | [5 empty] | bitmap
000D | 01 01 00 00 00 00 00 00; | reserved for ipad |  |  | d | 0x0b | xor relays |  | 0=accum, 1=value, 3=add1B, 4=add2B, 5=add4B | [5 empty] | bitmap
000E | 01 01 00 00 00 00 00 00; | reserved for ipad | 0x03 | Run task | d | 0x01 | NewTask Wait # tick |  | 2byte goto |  |  | tick | Run a separate thread
000F | 01 01 00 00 00 00 00 00; | reserved for ipad |  |  | d | 0x02 | Reuse Wait # tick |  | 2byte goto (acc->acc called) |  |  | tick | Relative, reuse of existing task if present updating tick (used for timeout interactive mode)
0010 | 01 01 00 00 00 00 00 00; | reserved for ipad |  |  | d | 0x03 | Reuse/WaitTick/OrigDev |  | 2byte goto (acc->acc called) |  |  | tick | Relative, reuse of existing task with same device if present updating tick (used for timeout interactive mode) [multidev]
0011 | 01 01 00 00 00 00 00 00; | reserved for ipad | 0x04 | Exit | d | 0x01 | Stop execution
0012 | 01 01 00 00 00 00 00 00; | reserved for ipad |  |  |  | 0x02 | Return to caller in accumulator
0013 | 01 01 00 00 00 00 00 00; | reserved for ipad | 0x05 | GoTo if acc[0] != | d |  | 0=acc, 1=value, 3=addr 1B, 4=addr 2B, 5=addr 4B | [6 empty] | 2byte goto |  | 4bytes value
0014 | 01 01 00 00 00 00 00 00; | reserved for ipad | 0x06 | GoTo if acc[0] > | d |  | 0=acc, 1=value, 3=addr 1B, 4=addr 2B, 5=addr 4B | [6 empty] | 2byte goto |  | 4bytes value
0015 | 01 01 00 00 00 00 00 00; | reserved for ipad | 0x07 | GoTo if acc[0] < | d |  | 0=acc, 1=value, 3=addr 1B, 4=addr 2B, 5=addr 4B | [6 empty] | 2byte goto |  | 4bytes value
0016 | 01 01 00 00 00 00 00 00; | reserved for ipad | 0x08 | GoTo if acc[0] = | d |  | 0=acc, 1=value, 3=addr 1B, 4=addr 2B, 5=addr 4B | [6 empty] | 2byte goto |  | 4bytes value
0017 | 01 01 B0 00 00 00 00 00; | goto #checkout | 0x09 | GoTo if acc[0] AND | d |  | 0=acc, 1=value, 3=addr 1B, 4=addr 2B, 5=addr 4B | [6 empty] | 2byte goto |  | 4bytes value |  |  | goto if a bit match
0018 | 01 01 D6 00 00 00 00 00; | goto #checkin | 0x10 | Mathematics | d | 0x01 | Add | 1=value, 2=RPN, 3=addr 1B, 4=addr 2B, 5=addr 4B | [5 empty] | empty | 4 byte value |  | 1 value is from last 4 bytes
0019 | 20 FF 00 00 00 00 00 00; | send.modbus $dev=server $reg=0 $dec=0 |  |  | d | 0x02 | Sub | 1=value, 2=RPN, 3=addr 1B, 4=addr 2B, 5=addr 4B | [5 empty] | empty | 4 byte value |  | 2 RPN operates in Accumulator and last stack, shift down 3 values in stack
001A | 21 01 00 06 02 BC 00 00; | send.modbus $type=idpg $reg=6 $dec=70*10 |  |  | d | 0x03 | Mul | 1=value, 2=RPN, 3=addr 1B, 4=addr 2B, 5=addr 4B | [5 empty] | empty | 4 byte value |  | 3-5 uses memory with 1,2,4 bytes
001B | 21 01 00 53 03 E8 00 00; | send.modbus $type=idpg $reg=83 $dec=100*10 |  |  | d | 0x04 | OR | 1=value, 2=RPN, 3=addr 1B, 4=addr 2B, 5=addr 4B | [5 empty] | empty | 4 byte value
001C | 21 03 00 0F 01 F4 00 00; | send.modbus $type=tag $reg=15 $dec=50*10 |  |  | d | 0x05 | XOR | 1=value, 2=RPN, 3=addr 1B, 4=addr 2B, 5=addr 4B | [5 empty] | empty | 4 byte value |  | Stack is 3 values + Accumulator like Forth
001D | 21 03 00 10 00 32 00 00; | send.modbus $type=tag $reg=16 $dec=5*10 |  |  | d | 0x06 | AND | 1=value, 2=RPN, 3=addr 1B, 4=addr 2B, 5=addr 4B | [5 empty] | empty | 4 byte value
001E | 21 03 00 11 03 20 00 00; | send.modbus $type=tag $reg=17 $dec=80*10 |  |  | d | 0x07 | << | 1=value, 2=RPN, 3=addr 1B, 4=addr 2B, 5=addr 4B | [5 empty] | empty | 4 byte value
001F | 21 03 00 12 00 32 00 00; | send.modbus $type=tag $reg=18 $dec=5*10 |  |  | d | 0x08 | >> | 1=value, 2=RPN, 3=addr 1B, 4=addr 2B, 5=addr 4B | [5 empty] | empty | 4 byte value |  |  | 1B=byte, 2B=16bit, 4B=32bit
0020 | 21 06 00 0F 03 20 00 00; | send.modbus $type=gsw $reg=15 $dec=80*10 |  |  | d | 0x09 | Div | 0=Acc, 1=value, 2=RPN, 3=addr 1B, 4=addr 2B, 5=addr 4B | [5 empty] | empty | 4 byte value |  | 3-5 uses memory with 1,2,4 bytes
0021 | 21 06 00 10 01 2C 00 00; | send.modbus $type=gsw $reg=16 $dec=30*10 |  |  | d | 0x0a | Mod | 0=Acc, 1=value, 2=RPN, 3=addr 1B, 4=addr 2B, 5=addr 4B | [5 empty] | empty | 4 byte value |  | 3-5 uses memory with 1,2,4 bytes
0022 | 03 01 2E 00 20 4E 00 00; | run #refresh_idpg $sec=2 |  |  | d | 0x80 | PUSH | 1=value,3=1B,4=2B, 5=4B,a=acc[0]=RTC(add), | [5 empty] | shiftYN | 4 byte value |  | 3-5= addr a-b uses RTC+acc[0]
0023 | 03 01 DD 00 F0 49 02 00; | run #tag_flash $sec=15 |  |  | d | [8 empty] | shiftYN | 1 item size |  | 1 byte relative positive address, 1 elements, 1 empty
0024 | 03 02 DB 04 50 C3 00 00; | reuse #dnd_relay $sec=5 |  |  | d | [8 empty] | shiftYN | 1 item size |  | 1 byte relative positive address, 1 elements, 1 empty
0025 | 03 02 AD 05 C0 27 09 00; | reuse #temp_probe_cycle $min=1 |  |  | d |  |  | e=CurrentEventDevice, f=addr 4B+OrigDevEnum(DeviceMap) | [5 empty] | shiftYN | 4 byte value
0026 | 03 02 A5 05 50 C3 00 00; | reuse #power_recover $sec=5 |  |  | d | 0x81 | POP | 3=1B,4=2B,5=4B,a=RTC(add)=acc[0],b=RTC(acc[0])=acc[1] | [5 empty] | shiftYN | 4 byte value
0027 | 04 01 00 00 00 00 00 00; | exit |  |  | d |  |  | e=CurrentEventDevice, f=addr 4B+OrigDevEnum(DeviceMap) | [5 empty] | shiftYN | 4 byte value
0028 | 40 01 01 00 00 00 00 00; | debug |  |  | d | 0x82 | PUSH time | [6 empty] | shiftYN
0029 | 04 01 00 00 00 00 00 00; | exit | 0x20 | Send ModBus 1 Word | d | Dest | PosHi | PosLo | Whi | Wlo | crcH | crcL |  | Dest FF=ServerIP, FE=OrigDevice |  |  |  |  | # dev map (Type=all devices with specified type)
002A | 22 FF 00 0E 10 00 00 00; | send.modbus $dev=server $reg=14 $len=16 | 0x21 | Send ModBus 1 Word | d | Type | PosHi | PosLo | Whi | Wlo | crcH | crcL |  | Dest FF=ServerIP, FE=OrigDevice |  |  |  |  | Send to all devices with type=x
002B | 04 01 00 00 00 00 00 00; | exit | 0x22 | Send ModBus Accumulator | d | Dest | PosHi | PosLo | bytes(2-16),NW |  | crcH | crcL |  | Dest FF=ServerIP, FE=OrigDevice |  |  |  |  | NW=no wait
002C | 22 FF 00 08 04 00 00 00; | send.modbus $dev=server $reg=8 $len=4 | 0x23 | Send ModBus Accumulator | d | Type | PosHi | PosLo | bytes(2-16),00 |  | crcH | crcL |  | Dest FF=ServerIP, FE=OrigDevice |  |  |  |  | Send to all devices with type=x
002D | 04 01 00 00 00 00 00 00; | exit | 0x26 | Read modbus in Accumulator | d | Dest | PosHi | PosLo | bytes(2,4), 00 |  | crcH | crcL |  | Dest FF=ServerIP, FE=OrigDevice
002E | 10 80 0A 00 16 00 00 00; | load $var=workflow | 0x2a | Seand modbus Acc[*] | d d d: d; PUSH time Whi Whi: Dest+PosH+PosL+Len (1b+1b+1b+1b+max 12b max message) |  | gateway |  | 02190003;c8 TAG SetPoint=200 ->35192835;200;0;0
002F | 10 80 0c 00 04 06 0a 00; | array table colors/blink | 0x2b | Read modbus Acc[0]->Acc[*] | d d d: d; PUSH time Whi Whi: Dest+PosH+PosL+Len |  | gateway |  | Reat TAG Setpoint 35192835;0;0;0
0030 | 22 01 00 04 04 00 00 00; | send.modbus $dev=idpg $reg=4 $len=4 | 0x30 | Call RCU Acc[*] | 0x82 Dest Type: Dest; PUSH time Whi Whi: Program address |  | Pass 4 register to the defined RCU device (+read ModBus 3 su TCP/IP)
0031 | 10 80 0A 00 16 00 00 00; | load $var=workflow
0032 | 10 80 0c 00 01 08 0a 00; | array table blink time | # | Notify packet | d d d: Parameters
0033 | 22 01 00 07 02 00 00 00; | send.modbus $dev=idpg $reg=7 $len=2 | 1 | Eartbeat | d d d: Counter
0034 | 04 01 00 00 00 00 00 00; | exit | 2 | Card Insert | d d d: CardId (8), Time
0035 | 00 54 00 00 55 54 00 00; | data1 colorblink | 3 | CardExtract | d d d: none
0036 | 14 54 0f 00 14 54 00 00; | data2 colorblink | 4 | Mur/Dnd | d d d: Status
0037 | 55 54 00 00 41 54 00 00; | data3 colorblink | 5 | OpenNOK | d d d: Status, Time
0038 | eb 54 00 00 aa a0 00 00; | data4 colorblink | 6 | Open OK | d d d: CardId (8), Time
0039 | aa a2 0f 00 ff 54 0f 00; | data5 colorblink | 7 | Read RTC Var | bar: d d d to PUSH time PosLo PosLo
003A | 00 18 18 00 00 00 00 00; | data1 blink time (ex 0 18) | 8 | Read modbus from device | bar: d d d to PUSH time PosLo PosLo
003B | 05 0a 00 00 00 00 00 00; | data2 blink time (ex 0 18) | bar: d d d to PUSH time PosLo PosLo
003C | 04 01 00 00 00 00 00 00; | exit | bar: d d d to PUSH time PosLo PosLo
003D | 10 80 0A 00 16 00 00 00; | load $var=workflow | bar: d d d to PUSH time PosLo PosLo
003E | 08 01 41 00 01 00 00 00; | if equal goto #+3 $dec=1
003F | 10 80 01 00 00 00 00 00; | load $dec=0
0040 | 01 01 42 00 00 00 00 00; | goto #+2
0041 | 10 80 01 00 40 50 00 00; | load $hex=5040
0042 | 22 01 00 04 04 00 00 00; | send.modbus $dev=idpg $reg=4 $len=4
0043 | 03 02 93 00 00 00 00 00; | reuse #idpg_relay_bell
0044 | 01 01 00 00 10 27 00 00; | wait $sec=1
0045 | 03 02 2E 00 00 00 00 00; | reuse #refresh_idpg
0046 | 04 01 00 00 00 00 00 00; | exit
0047 | 20 FF 00 0F 00 01 00 00; | send.modbus $dev=server $reg=15 $hex=0001
0048 | 03 02 96 00 00 00 00 00; | reuse #set_lock_action
0049 | 20 01 00 04 55 55 00 00; | send.modbus $dev=idpg $reg=4 $hex=5555
004A | 10 06 01 00 FF 00 00 00; | math.and $hex=ff
004B | 08 01 4E 00 01 00 00 00; | if equal #+3 $hex=1
004C | 10 80 01 00 01 00 00 00; | load $hex=1
004D | 01 01 4F 00 00 00 00 00; | goto #+2
004E | 10 80 01 00 10 00 00 00; | load $hex=10
004F | 22 FF 00 06 10 00 00 00; | send.modbus $dev=server $reg=6 $len=16
0050 | 10 80 01 00 01 00 00 00; | load $hex=1
0051 | 10 81 0A 00 81 00 00 00; | save $var=temp_user
0052 | 03 02 2E 00 10 27 00 00; | reuse #refresh_idpg $sec=1
0053 | 10 80 0A 00 15 00 00 00; | load $var=user
0054 | 08 0A 8E 00 81 00 00 00; | if equal goto #exit $var=temp_user
0055 | 10 80 0A 00 81 00 00 00; | load $var=temp_user
0056 | 10 81 0A 00 15 00 00 00; | save $var=user
0057 | 22 02 00 05 02 00 00 00; | send.modbus $dev=2 $reg=5 $len=2
0058 | 22 03 00 05 02 00 00 00; | send.modbus $dev=3 $reg=5 $len=2
0059 | 22 04 00 05 02 00 00 00; | send.modbus $dev=4 $reg=5 $len=2
005A | 10 80 01 00 00 00 00 00; | load $hex=0
005B | 22 FF 00 02 10 00 00 00; | send.modbus $dev=server $reg=2 $len=16
005C | 10 80 01 00 11 00 00 00; | load $hex=11
005D | 10 81 0A 00 12 00 00 00; | save $var=season
005E | 10 80 0A 00 15 00 00 00; | load $var=user
005F | 08 01 6D 00 10 00 00 00; | if equal #staff_welcome $hex=10
0060 | 10 80 0A 00 84 00 00 00; | load $var=rcu2_relays
0061 | 10 04 01 00 00 F2 00 00; | math.or $relay=10,13-16
0062 | 10 81 0A 00 84 00 00 00; | save $var=rcu2_relays
0063 | 22 02 00 07 02 00 00 00; | send.modbus $dev=2 $reg=7 $len=2
0064 | 10 80 0A 00 85 00 00 00; | load $var=rcu3_relays
0065 | 10 04 01 00 80 00 00 00; | math.or $relay=8
0066 | 10 81 0A 00 85 00 00 00; | save $var=rcu3_relays
0067 | 22 03 00 07 02 00 00 00; | send.modbus $dev=3 $reg=7 $len=2
0068 | 10 80 0A 00 86 00 00 00; | load $var=rcu4_relays
0069 | 10 04 01 00 18 C0 00 00; | math.or $relay=4,5,15,16
006A | 10 81 0A 00 86 00 00 00; | save $var=rcu4_relays
006B | 22 04 00 07 02 00 00 00; | send.modbus $dev=4 $reg=7 $len=2
006C | 01 01 79 00 00 00 00 00; | goto #common_welcome
006D | 10 80 0A 00 84 00 00 00; | load $var=rcu2_relays
006E | 10 04 01 00 FF FF 00 00; | math.or $relay=1-16
006F | 10 81 0A 00 84 00 00 00; | save $var=rcu2_relays
0070 | 22 02 00 07 02 00 00 00; | send.modbus $dev=2 $reg=7 $len=2
0071 | 10 80 0A 00 85 00 00 00; | load $var=rcu3_relays
0072 | 10 04 01 00 FF FF 00 00; | math.or $relay=1-16
0073 | 10 81 0A 00 85 00 00 00; | save $var=rcu3_relays
0074 | 22 03 00 07 02 00 00 00; | send.modbus $dev=3 $reg=7 $len=2
0075 | 10 80 0A 00 86 00 00 00; | load $var=rcu4_relays
0076 | 10 04 01 00 78 FF 00 00; | math.or $relay=4-7,9-16
0077 | 10 81 0A 00 86 00 00 00; | save $var=rcu4_relays
0078 | 22 04 00 07 02 00 00 00; | send.modbus $dev=4 $reg=7 $len=2
0079 | 10 80 0A 00 0D 00 00 00; | load $var=temp2
007A | 22 06 00 19 02 00 00 00; | send.modbus $dev=tag2 $reg=25 $len=2
007B | 03 03 74 01 00 00 00 06; | reuse #refresh_tag2 $dev=tag2
007C | 10 80 0A 00 0E 00 00 00; | load $var=temp3
007D | 22 07 00 19 02 00 00 00; | send.modbus $dev=tag3 $reg=25 $len=2
007E | 03 03 A3 01 00 00 00 07; | reuse #refresh_tag3 $dev=tag3
007F | 10 80 0A 00 0F 00 00 00; | load $var=temp4
0080 | 22 08 00 19 02 00 00 00; | send.modbus $dev=tag4 $reg=25 $len=2
0081 | 03 03 D2 01 00 00 00 08; | reuse #refresh_tag4 $dev=tag4
0082 | 10 80 0A 00 10 00 00 00; | load $var=temp5
0083 | 22 09 00 19 02 00 00 00; | send.modbus $dev=tag5 $reg=25 $len=2
0084 | 03 03 01 02 00 00 00 09; | reuse #refresh_tag5 $dev=tag5
0085 | 02 08 00 00 00 00 00 00; | rcu.read input
0086 | 10 05 01 00 02 00 00 00; | math.xor $bit=2
0087 | 09 01 8E 00 02 00 00 00; | if bit true #exit $bit=2
0088 | 10 80 0A 00 0C 00 00 00; | load $var=temp1
0089 | 22 05 00 19 02 00 00 00; | send.modbus $dev=tag1 $reg=25 $len=2
008A | 10 80 0A 00 11 00 00 00; | load $var=temp6
008B | 22 0A 00 19 02 00 00 00; | send.modbus $dev=tag6 $reg=25 $len=2
008C | 03 03 F9 00 00 00 00 05; | reuse #refresh_tag1 $dev=tag1
008D | 03 03 30 02 00 00 00 0A; | reuse #refresh_tag6 $dev=tag6
008E | 04 01 00 00 00 00 00 00; | exit
008F | 22 FF 00 05 10 00 00 00; | send.modbus $dev=server $reg=5 $len=16
0090 | 20 01 00 04 AA AA 00 00; | send.modbus $dev=idpg $reg=4 $hex=aaaa
0091 | 03 02 2E 00 10 27 00 00; | reuse #refresh_idpg $sec=1
0092 | 04 01 00 00 00 00 00 00; | exit
0093 | 10 80 01 00 01 00 00 00; | load $hex=1
0094 | 22 04 00 0B 02 00 00 00; | send.modbus $dev=4 $reg=11 $len=2
0095 | 04 01 00 00 00 00 00 00; | exit
0096 | 10 80 01 00 01 00 00 00; | load $dec=1
0097 | 10 81 0A 00 83 00 00 00; | save $var=lockaction
0098 | 03 02 9A 00 C0 27 09 00; | reuse #unset_lock_action $sec=60
0099 | 04 01 00 00 00 00 00 00; | exit
009A | 10 80 01 00 00 00 00 00; | load $hex=0
009B | 10 81 0A 00 83 00 00 00; | save $var=lockaction
009C | 04 01 00 00 00 00 00 00; | exit
009D | 10 80 0A 00 83 00 00 00; | load $var=lockaction
009E | 05 01 A3 00 00 00 00 00; | if not equal #exit $hex=0
009F | 20 FF 00 0F 00 04 00 00; | send.modbus $dev=server $reg=15 $hex=0004
00A0 | 10 80 0A 00 05 00 00 00; | load $var=checkin
00A1 | 08 01 4C 00 01 00 00 00; | if equal #door_contact_override_guest $dec=1
00A2 | 01 01 4E 00 00 00 00 00; | goto #door_contact_override_staff
00A3 | 04 01 00 00 00 00 00 00; | exit
00A4 | 10 80 0A 00 83 00 00 00; | load $var=lockaction
00A5 | 05 01 A8 00 00 00 00 00; | if not equal #exit $hex=0
00A6 | 20 FF 00 0F 00 00 00 00; | send.modbus $dev=server $reg=15 $hex=0000
00A7 | 03 02 AC 00 A0 86 01 00; | reuse #door_close_delayed $sec=10
00A8 | 04 01 00 00 00 00 00 00; | exit
00A9 | 20 FF 00 0F 00 00 00 00; | send.modbus $dev=server $reg=15 $hex=0000
00AA | 03 02 AC 00 A0 86 01 00; | reuse #door_close_delayed $sec=10
00AB | 04 01 00 00 00 00 00 00; | exit
00AC | 10 80 01 00 00 00 00 00; | load $dec=0
00AD | 10 81 0A 00 80 00 00 00; | save $var=last_action
00AE | 03 03 30 05 40 0D 03 05; | reuse #check_exit_scene $sec=20 $dev=tag1
00AF | 04 01 00 00 00 00 00 00; | exit
00B0 | 10 80 01 00 02 00 00 00; | load $hex=2
00B1 | 22 FF 00 03 10 00 00 00; | send.modbus $dev=server $reg=3 $len=16
00B2 | 10 80 01 00 00 00 00 00; | load $hex=0
00B3 | 10 81 0A 00 84 00 00 00; | save $var=rcu2_relays
00B4 | 22 02 00 07 02 00 00 00; | send.modbus $dev=2 $reg=7 $len=2
00B5 | 10 80 0A 00 06 00 00 00; | load $var=thermo1
00B6 | 22 04 00 09 02 00 00 00; | send.modbus $dev=4 $reg=9 $len=2
00B7 | 10 80 0A 00 0C 00 00 00; | load $var=temp1
00B8 | 22 04 00 0A 02 00 00 00; | send.modbus $dev=4 $reg=10 $len=2
00B9 | 01 01 00 00 20 4E 00 00; | wait $sec=2
00BA | 10 80 01 00 00 00 00 00; | load $dec=0
00BB | 10 81 0A 00 15 00 00 00; | save $var=user
00BC | 10 81 0A 00 81 00 00 00; | save $var=temp_user
00BD | 10 81 0A 00 16 00 00 00; | save $var=workflow
00BE | 10 81 0A 00 85 00 00 00; | save $var=rcu3_relays
00BF | 10 81 0A 00 86 00 00 00; | save $var=rcu4_relays
00C0 | 22 02 00 06 02 00 00 00; | send.modbus $dev=2 $reg=6 $len=2
00C1 | 01 01 00 00 DC 05 00 00; | wait $sec=0.15
00C2 | 22 03 00 06 02 00 00 00; | send.modbus $dev=3 $reg=6 $len=2
00C3 | 22 FF 00 04 03 00 00 00; | send.modbus $dev=server $reg=4 $len=3
00C4 | 22 02 00 05 02 00 00 00; | send.modbus $dev=2 $reg=5 $len=2
00C5 | 01 01 00 00 DC 05 00 00; | wait $sec=0.15
00C6 | 22 03 00 05 02 00 00 00; | send.modbus $dev=3 $reg=5 $len=2
00C7 | 22 04 00 05 02 00 00 00; | send.modbus $dev=4 $reg=5 $len=2
00C8 | 10 80 01 00 01 00 00 00; | load $hex=01
00C9 | 10 81 0A 00 12 00 00 00; | save $var=season
00CA | 10 80 0A 00 84 00 00 00; | load $var=rcu2_relays
00CB | 10 06 01 00 00 C0 FF FF; | math.and $relay=1-14
00CC | 10 81 0A 00 84 00 00 00; | save $var=rcu2_relays
00CD | 22 02 00 07 02 00 00 00; | send.modbus $dev=2 $reg=7 $len=2
00CE | 10 80 01 00 00 00 00 00; | load $hex=0
00CF | 22 03 00 07 02 00 00 00; | send.modbus $dev=3 $reg=7 $len=2
00D0 | 10 80 01 00 00 00 00 00; | load $hex=0
00D1 | 22 04 00 07 02 00 00 00; | send.modbus $dev=4 $reg=7 $len=2
00D2 | 03 02 2E 00 00 00 00 00; | reuse #refresh_idpg
00D3 | 03 02 DB 04 00 00 00 00; | reuse #dnd_relay
00D4 | 01 01 4E 05 00 00 00 00; | goto #tag_conditional_check_without_user
00D5 | 04 01 00 00 00 00 00 00; | exit
00D6 | 10 80 01 00 01 00 00 00; | load $hex=1
00D7 | 22 FF 00 03 10 00 00 00; | send.modbus $dev=server $reg=3 $len=16
00D8 | 10 80 01 00 00 C0 00 00; | load $relay=15,16
00D9 | 10 81 0A 00 84 00 00 00; | save $var=rcu2_relays
00DA | 22 02 00 07 02 00 00 00; | send.modbus $dev=2 $reg=7 $len=2
00DB | 01 01 B5 00 00 00 00 00; | goto #checkout_common
00DC | 04 01 00 00 00 00 00 00; | exit
00DD | 10 80 0A 00 27 00 00 00; | load $var=tag_minmax
00DE | 05 01 E1 00 00 00 00 00; | if not equal #+3 $hex=0
00DF | 10 80 01 00 1C 13 00 00; | load $dec=19*256+28
00E0 | 10 81 0A 00 27 00 00 00; | save $var=tag_minmax
00E1 | 23 03 00 06 02 00 00 00; | send.modbus $type=tag $reg=6 $len=2
00E2 | 03 02 F0 00 00 00 00 00; | reuse #min_fan_speed_check
00E3 | 10 80 01 00 32 00 5E 01; | load $dec=65536*35*10+5*10
00E4 | 10 81 0A 00 04 00 00 00; | save $var=anti_ice
00E5 | 10 80 01 00 01 00 05 00; | load $dec=65536*0.5*10+0.1*10
00E6 | 10 81 0A 00 13 00 00 00; | save $var=intervention
00E7 | 21 03 00 03 00 02 00 00; | send.modbus $type=tag $reg=3 $dec=2
00E8 | 01 01 00 00 64 00 00 00; | wait $sec=0.01
00E9 | 21 03 00 08 00 02 00 00; | send.modbus $type=tag $reg=8 $hex=2
00EA | 10 80 0A 00 15 00 00 00; | load $var=user
00EB | 09 01 EE 00 FF 00 00 00; | if bit true #+3 $hex=ff
00EC | 03 02 4E 05 00 00 00 00; | reuse #tag_conditional_check_without_user
00ED | 04 01 00 00 00 00 00 00; | exit
00EE | 03 02 79 00 00 00 00 00; | reuse #tag_conditional_check_with_user
00EF | 04 01 00 00 00 00 00 00; | exit
00F0 | 10 80 0A 00 15 00 00 00; | load $var=user
00F1 | 09 01 F5 00 FF 00 00 00; | if bit true #+4 $hex=ff
00F2 | 10 80 01 00 01 00 00 00; | load $hex=01
00F3 | 10 81 0A 00 12 00 00 00; | save $var=season
00F4 | 04 01 00 00 00 00 00 00; | exit
00F5 | 10 80 01 00 11 00 00 00; | load $hex=11
00F6 | 10 81 0A 00 12 00 00 00; | save $var=season
00F7 | 04 01 00 00 00 00 00 00; | exit
00F8 | 01 01 00 00 00 00 00 00; | run #bedroom_master @rcu2
00F9 | 10 80 0A 00 06 00 00 00; | load $var=thermo1
00FA | 10 06 01 00 AA AA 00 00; | math.and $hex=aaaa
00FB | 08 01 FD 00 80 00 00 00; | if equal #+2 $hex=80
00FC | 10 08 01 00 01 00 00 00; | math.shiftr $dec=1
00FD | 22 05 00 0D 04 00 00 00; | send.modbus $dev=tag1 $reg=13 $len=4
00FE | 04 01 00 00 00 00 00 00; | exit
00FF | 02 08 00 00 00 00 00 00; | rcu.read input
0100 | 10 05 01 00 02 00 00 00; | math.xor $bit=2
0101 | 09 01 25 01 02 00 00 00; | if bit true #exit $bit=2
0102 | 20 FF 00 0D 00 01 00 00; | send.modbus $dev=server $reg=13 $hex=0001
0103 | 10 80 01 00 55 06 3F 00; | load $fan=fan1
0104 | 01 01 22 01 00 00 00 00; | goto #tag1_common
0105 | 02 08 00 00 00 00 00 00; | rcu.read input
0106 | 10 05 01 00 02 00 00 00; | math.xor $bit=2
0107 | 09 01 25 01 02 00 00 00; | if bit true #exit $bit=2
0108 | 20 FF 00 0D 00 02 00 00; | send.modbus $dev=server $reg=13 $hex=0002
0109 | 10 80 01 00 65 05 3F 00; | load $fan=fan2
010A | 01 01 22 01 00 00 00 00; | goto #tag1_common
010B | 02 08 00 00 00 00 00 00; | rcu.read input
010C | 10 05 01 00 02 00 00 00; | math.xor $bit=2
010D | 09 01 25 01 02 00 00 00; | if bit true #exit $bit=2
010E | 20 FF 00 0D 00 03 00 00; | send.modbus $dev=server $reg=13 $hex=0003
010F | 10 80 01 00 56 05 3F 00; | load $fan=fan3
0110 | 01 01 22 01 00 00 00 00; | goto #tag1_common
0111 | 02 08 00 00 00 00 00 00; | rcu.read input
0112 | 10 05 01 00 02 00 00 00; | math.xor $bit=2
0113 | 09 01 25 01 02 00 00 00; | if bit true #exit $bit=2
0114 | 20 FF 00 0D 00 04 00 00; | send.modbus $dev=server $reg=13 $hex=0004
0115 | 10 80 01 00 55 09 3F 00; | load $fan=auto
0116 | 01 01 22 01 00 00 00 00; | goto #tag1_common
0117 | 02 08 00 00 00 00 00 00; | rcu.read input
0118 | 10 05 01 00 02 00 00 00; | math.xor $bit=2
0119 | 09 01 25 01 02 00 00 00; | if bit true #exit $bit=2
011A | 20 FF 00 0D 00 05 00 00; | send.modbus $dev=server $reg=13 $hex=0005
011B | 10 80 01 00 95 05 3F 00; | load $fan=eco
011C | 01 01 22 01 00 00 00 00; | goto #tag1_common
011D | 02 08 00 00 00 00 00 00; | rcu.read input
011E | 10 05 01 00 02 00 00 00; | math.xor $bit=2
011F | 09 01 25 01 02 00 00 00; | if bit true #exit $bit=2
0120 | 20 FF 00 0D 00 06 00 00; | send.modbus $dev=server $reg=13 $hex=0006
0121 | 10 80 01 00 59 05 3F 00; | load $fan=off
0122 | 10 81 0A 00 06 00 00 00; | save $var=thermo1
0123 | 22 05 00 0D 04 00 00 00; | send.modbus $dev=tag1 $reg=13 $len=4
0124 | 03 02 F9 00 F0 49 02 00; | reuse #refresh_tag1 $sec=15
0125 | 04 01 00 00 00 00 00 00; | exit
0126 | 10 80 0A 00 06 00 00 00; | load $var=thermo1
0127 | 22 05 00 0D 04 00 00 00; | send.modbus $dev=tag1 $reg=13 $len=4
0128 | 03 02 F9 00 F0 49 02 00; | reuse #refresh_tag1 $sec=15
0129 | 04 01 00 00 00 00 00 00; | exit
012A | 02 08 00 00 00 00 00 00; | rcu.read input
012B | 10 05 01 00 02 00 00 00; | math.xor $bit=2
012C | 09 01 33 01 02 00 00 00; | if bit true #exit $bit=2
012D | 03 02 26 01 00 00 00 00; | reuse #tag1_wakeup
012E | 01 01 00 00 60 EA 00 00; | wait $sec=6
012F | 26 05 00 19 02 00 00 00; | read.modbus $dev=tag1 $reg=25
0130 | 10 81 0A 00 0C 00 00 00; | save $var=temp1
0131 | 10 80 10 01 00 00 00 00; | load shift enum
0132 | 22 FF 00 0B 08 00 00 00; | send.modbus $dev=server $reg=11 $len=8
0133 | 04 01 00 00 00 00 00 00; | exit
0134 | 01 01 00 00 20 4E 00 00; | wait $sec=2
0135 | 10 80 0A 00 14 00 00 00; | load $var=room_empty
0136 | 07 01 39 01 00 80 00 00; | if less than #+3 $hex=8000
0137 | 10 06 01 00 FF 7F FF FF; | math.and $relay=16
0138 | 10 01 0A 00 0C 00 00 00; | math.add $var=temp1
0139 | 22 05 00 19 02 00 00 00; | send.modbus $dev=tag1 $reg=25 $len=2
013A | 04 01 00 00 00 00 00 00; | exit
013B | 10 80 01 00 01 00 00 00; | load $hex=1
013C | 01 01 80 05 00 00 00 00; | goto #set_last_action
013D | 20 FF 00 0C 00 01 00 00; | send.modbus $dev=server $reg=12 $hex=001
013E | 01 01 00 00 64 00 00 00; | wait $sec=0.01
013F | 20 FF 00 0C 05 01 00 00; | send.modbus $dev=server $reg=12 $hex=501
0140 | 03 03 F9 00 00 00 00 05; | reuse #refresh_tag1 $dev=tag1
0141 | 03 03 30 02 00 00 00 0A; | reuse #refresh_tag6 $dev=tag6
0142 | 03 02 44 01 50 C3 00 00; | reuse #delay_window_open $sec=5
0143 | 04 01 00 00 00 00 00 00; | exit
0144 | 02 08 00 00 00 00 00 00; | rcu.read input
0145 | 09 01 59 01 02 00 00 00; | if bit true #exit $bit=2
0146 | 10 80 0A 00 06 00 00 00; | load $var=thermo1
0147 | 08 01 59 01 00 20 00 00; | if equal #exit $hex=2000
0148 | 10 80 0A 00 06 00 00 00; | load $var=thermo1
0149 | 10 81 0A 00 87 00 00 00; | save $var=backup_thermo1
014A | 10 80 0A 00 0B 00 00 00; | load $var=thermo6
014B | 10 81 0A 00 88 00 00 00; | save $var=backup_thermo6
014C | 20 05 00 03 00 06 00 00; | send.modbus $dev=tag1 $reg=3 $hex=6
014D | 01 01 00 00 64 00 00 00; | wait $sec=0.01
014E | 20 0A 00 03 00 06 00 00; | send.modbus $dev=tag6 $reg=3 $hex=6
014F | 10 80 01 00 00 20 00 00; | load $hex=2000
0150 | 10 81 0A 00 06 00 00 00; | save $var=thermo1
0151 | 10 81 0A 00 0B 00 00 00; | save $var=thermo6
0152 | 51 01 00 00 88 13 00 00; | rcu.dim aout1 $lum=0% $sec=0.5
0153 | 10 80 01 00 01 00 00 00; | load $hex=1
0154 | 10 80 01 01 00 00 32 00; | load dimmer $lum=0% $sec=0.5
0155 | 22 0C 00 0C 06 00 00 00; | send.modbus $dev=ioexp2 $reg=12 $len=6
0156 | 10 80 01 00 08 00 00 00; | load $hex=8
0157 | 22 05 00 0D 04 00 00 00; | send.modbus $dev=tag1 $reg=13 $len=4
0158 | 22 0A 00 0D 04 00 00 00; | send.modbus $dev=tag6 $reg=13 $len=4
0159 | 04 01 00 00 00 00 00 00; | exit
015A | 20 FF 00 0C 00 00 00 00; | send.modbus $dev=server $reg=12 $hex=000
015B | 01 01 00 00 64 00 00 00; | wait $sec=0.01
015C | 20 FF 00 0C 05 00 00 00; | send.modbus $dev=server $reg=12 $hex=500
015D | 03 02 5F 01 50 C3 00 00; | reuse #delay_window_close $sec=5
015E | 04 01 00 00 00 00 00 00; | exit
015F | 02 08 00 00 00 00 00 00; | rcu.read input
0160 | 10 05 01 00 02 00 00 00; | math.xor $bit=2
0161 | 09 01 70 01 02 00 00 00; | if bit true #exit $bit=2
0162 | 10 80 0A 00 06 00 00 00; | load $var=thermo1
0163 | 05 01 70 01 00 20 00 00; | if not equal #exit $hex=2000
0164 | 10 80 0A 00 87 00 00 00; | load $var=backup_thermo1
0165 | 10 81 0A 00 06 00 00 00; | save $var=thermo1
0166 | 10 80 0A 00 88 00 00 00; | load $var=backup_thermo6
0167 | 10 81 0A 00 0B 00 00 00; | save $var=thermo6
0168 | 20 05 00 03 00 02 00 00; | send.modbus $dev=tag1 $reg=3 $hex=2
0169 | 01 01 00 00 64 00 00 00; | wait $sec=0.01
016A | 20 0A 00 03 00 02 00 00; | send.modbus $dev=tag6 $reg=3 $hex=2
016B | 10 80 0A 00 15 00 00 00; | load $var=user
016C | 05 01 71 01 00 00 00 00; | if not equal #+5 $hex=0
016D | 10 80 01 00 80 00 00 00; | load $hex=80
016E | 22 05 00 0D 04 00 00 00; | send.modbus $dev=tag1 $reg=13 $len=4
016F | 22 0A 00 0D 04 00 00 00; | send.modbus $dev=tag6 $reg=13 $len=4
0170 | 04 01 00 00 00 00 00 00; | exit
0171 | 03 03 F9 00 00 00 00 05; | reuse #refresh_tag1 $dev=tag1
0172 | 03 03 30 02 00 00 00 0A; | reuse #refresh_tag6 $dev=tag6
0173 | 04 01 00 00 00 00 00 00; | exit
0174 | 10 80 0A 00 07 00 00 00; | load $var=thermo2
0175 | 10 06 01 00 AA AA 00 00; | math.and $hex=aaaa
0176 | 08 01 78 01 80 00 00 00; | if equal #+2 $hex=80
0177 | 10 08 01 00 01 00 00 00; | math.shiftr $dec=1
0178 | 22 06 00 0D 04 00 00 00; | send.modbus $dev=tag2 $reg=13 $len=4
0179 | 04 01 00 00 00 00 00 00; | exit
017A | 20 FF 00 0D 01 01 00 00; | send.modbus $dev=server $reg=13 $hex=0101
017B | 10 80 01 00 55 06 3F 00; | load $fan=fan1
017C | 01 01 8B 01 00 00 00 00; | goto #tag2_common
017D | 20 FF 00 0D 01 02 00 00; | send.modbus $dev=server $reg=13 $hex=0102
017E | 10 80 01 00 65 05 3F 00; | load $fan=fan2
017F | 01 01 8B 01 00 00 00 00; | goto #tag2_common
0180 | 20 FF 00 0D 01 03 00 00; | send.modbus $dev=server $reg=13 $hex=0103
0181 | 10 80 01 00 56 05 3F 00; | load $fan=fan3
0182 | 01 01 8B 01 00 00 00 00; | goto #tag2_common
0183 | 20 FF 00 0D 01 04 00 00; | send.modbus $dev=server $reg=13 $hex=0104
0184 | 10 80 01 00 55 09 3F 00; | load $fan=auto
0185 | 01 01 8B 01 00 00 00 00; | goto #tag2_common
0186 | 20 FF 00 0D 01 05 00 00; | send.modbus $dev=server $reg=13 $hex=0105
0187 | 10 80 01 00 95 05 3F 00; | load $fan=eco
0188 | 01 01 8B 01 00 00 00 00; | goto #tag2_common
0189 | 20 FF 00 0D 01 06 00 00; | send.modbus $dev=server $reg=13 $hex=0106
018A | 10 80 01 00 59 05 3F 00; | load $fan=off
018B | 10 81 0A 00 07 00 00 00; | save $var=thermo2
018C | 22 06 00 0D 04 00 00 00; | send.modbus $dev=tag2 $reg=13 $len=4
018D | 03 02 74 01 F0 49 02 00; | reuse #refresh_tag2 $sec=15
018E | 04 01 00 00 00 00 00 00; | exit
018F | 10 80 0A 00 07 00 00 00; | load $var=thermo2
0190 | 22 06 00 0D 04 00 00 00; | send.modbus $dev=tag2 $reg=13 $len=4
0191 | 03 02 74 01 F0 49 02 00; | reuse #refresh_tag2 $sec=15
0192 | 04 01 00 00 00 00 00 00; | exit
0193 | 03 02 8F 01 00 00 00 00; | reuse #tag2_wakeup
0194 | 01 01 00 00 60 EA 00 00; | wait $sec=6
0195 | 26 06 00 19 02 00 00 00; | read.modbus $dev=tag2 $reg=25
0196 | 10 81 0A 00 0D 00 00 00; | save $var=temp2
0197 | 10 80 10 01 00 00 00 00; | load shift enum
0198 | 22 FF 00 0B 08 00 00 00; | send.modbus $dev=server $reg=11 $len=8
0199 | 04 01 00 00 00 00 00 00; | exit
019A | 01 01 00 00 20 4E 00 00; | wait $sec=2
019B | 10 80 0A 00 14 00 00 00; | load $var=room_empty
019C | 07 01 9F 01 00 80 00 00; | if less than #+3 $hex=8000
019D | 10 06 01 00 FF 7F FF FF; | math.and $relay=16
019E | 10 01 0A 00 0D 00 00 00; | math.add $var=temp2
019F | 22 06 00 19 02 00 00 00; | send.modbus $dev=tag2 $reg=25 $len=2
01A0 | 04 01 00 00 00 00 00 00; | exit
01A1 | 10 80 01 00 01 00 00 00; | load $hex=1
01A2 | 01 01 80 05 00 00 00 00; | goto #set_last_action
01A3 | 10 80 0A 00 08 00 00 00; | load $var=thermo3
01A4 | 10 06 01 00 AA AA 00 00; | math.and $hex=aaaa
01A5 | 08 01 A7 01 80 00 00 00; | if equal #+2 $hex=80
01A6 | 10 08 01 00 01 00 00 00; | math.shiftr $dec=1
01A7 | 22 07 00 0D 04 00 00 00; | send.modbus $dev=tag3 $reg=13 $len=4
01A8 | 04 01 00 00 00 00 00 00; | exit
01A9 | 20 FF 00 0D 02 01 00 00; | send.modbus $dev=server $reg=13 $hex=0201
01AA | 10 80 01 00 55 06 3F 00; | load $fan=fan1
01AB | 01 01 BA 01 00 00 00 00; | goto #tag3_common
01AC | 20 FF 00 0D 02 02 00 00; | send.modbus $dev=server $reg=13 $hex=0202
01AD | 10 80 01 00 65 05 3F 00; | load $fan=fan2
01AE | 01 01 BA 01 00 00 00 00; | goto #tag3_common
01AF | 20 FF 00 0D 02 03 00 00; | send.modbus $dev=server $reg=13 $hex=0203
01B0 | 10 80 01 00 56 05 3F 00; | load $fan=fan3
01B1 | 01 01 BA 01 00 00 00 00; | goto #tag3_common
01B2 | 20 FF 00 0D 02 04 00 00; | send.modbus $dev=server $reg=13 $hex=0204
01B3 | 10 80 01 00 55 09 3F 00; | load $fan=auto
01B4 | 01 01 BA 01 00 00 00 00; | goto #tag3_common
01B5 | 20 FF 00 0D 02 05 00 00; | send.modbus $dev=server $reg=13 $hex=0205
01B6 | 10 80 01 00 95 05 3F 00; | load $fan=eco
01B7 | 01 01 BA 01 00 00 00 00; | goto #tag3_common
01B8 | 20 FF 00 0D 02 06 00 00; | send.modbus $dev=server $reg=13 $hex=0206
01B9 | 10 80 01 00 59 05 3F 00; | load $fan=off
01BA | 10 81 0A 00 08 00 00 00; | save $var=thermo3
01BB | 22 07 00 0D 04 00 00 00; | send.modbus $dev=tag3 $reg=13 $len=4
01BC | 03 02 A3 01 F0 49 02 00; | reuse #refresh_tag3 $sec=15
01BD | 04 01 00 00 00 00 00 00; | exit
01BE | 10 80 0A 00 08 00 00 00; | load $var=thermo3
01BF | 22 07 00 0D 04 00 00 00; | send.modbus $dev=tag3 $reg=13 $len=4
01C0 | 03 02 A3 01 F0 49 02 00; | reuse #refresh_tag3 $sec=15
01C1 | 04 01 00 00 00 00 00 00; | exit
01C2 | 03 02 BE 01 00 00 00 00; | reuse #tag3_wakeup
01C3 | 01 01 00 00 60 EA 00 00; | wait $sec=6
01C4 | 26 07 00 19 02 00 00 00; | read.modbus $dev=tag3 $reg=25
01C5 | 10 81 0A 00 0E 00 00 00; | save $var=temp3
01C6 | 10 80 10 01 00 00 00 00; | load shift enum
01C7 | 22 FF 00 0B 08 00 00 00; | send.modbus $dev=server $reg=11 $len=8
01C8 | 04 01 00 00 00 00 00 00; | exit
01C9 | 01 01 00 00 20 4E 00 00; | wait $sec=2
01CA | 10 80 0A 00 14 00 00 00; | load $var=room_empty
01CB | 07 01 CE 01 00 80 00 00; | if less than #+3 $hex=8000
01CC | 10 06 01 00 FF 7F FF FF; | math.and $relay=16
01CD | 10 01 0A 00 0E 00 00 00; | math.add $var=temp3
01CE | 22 07 00 19 02 00 00 00; | send.modbus $dev=tag3 $reg=25 $len=2
01CF | 04 01 00 00 00 00 00 00; | exit
01D0 | 10 80 01 00 01 00 00 00; | load $hex=1
01D1 | 01 01 80 05 00 00 00 00; | goto #set_last_action
01D2 | 10 80 0A 00 09 00 00 00; | load $var=thermo4
01D3 | 10 06 01 00 AA AA 00 00; | math.and $hex=aaaa
01D4 | 08 01 D6 01 80 00 00 00; | if equal #+2 $hex=80
01D5 | 10 08 01 00 01 00 00 00; | math.shiftr $dec=1
01D6 | 22 08 00 0D 04 00 00 00; | send.modbus $dev=tag4 $reg=13 $len=4
01D7 | 04 01 00 00 00 00 00 00; | exit
01D8 | 20 FF 00 0D 03 01 00 00; | send.modbus $dev=server $reg=13 $hex=0301
01D9 | 10 80 01 00 55 06 3F 00; | load $fan=fan1
01DA | 01 01 E9 01 00 00 00 00; | goto #tag4_common
01DB | 20 FF 00 0D 03 02 00 00; | send.modbus $dev=server $reg=13 $hex=0302
01DC | 10 80 01 00 65 05 3F 00; | load $fan=fan2
01DD | 01 01 E9 01 00 00 00 00; | goto #tag4_common
01DE | 20 FF 00 0D 03 03 00 00; | send.modbus $dev=server $reg=13 $hex=0303
01DF | 10 80 01 00 56 05 3F 00; | load $fan=fan3
01E0 | 01 01 E9 01 00 00 00 00; | goto #tag4_common
01E1 | 20 FF 00 0D 03 04 00 00; | send.modbus $dev=server $reg=13 $hex=0304
01E2 | 10 80 01 00 55 09 3F 00; | load $fan=auto
01E3 | 01 01 E9 01 00 00 00 00; | goto #tag4_common
01E4 | 20 FF 00 0D 03 05 00 00; | send.modbus $dev=server $reg=13 $hex=0305
01E5 | 10 80 01 00 95 05 3F 00; | load $fan=eco
01E6 | 01 01 E9 01 00 00 00 00; | goto #tag4_common
01E7 | 20 FF 00 0D 03 06 00 00; | send.modbus $dev=server $reg=13 $hex=0306
01E8 | 10 80 01 00 59 05 3F 00; | load $fan=off
01E9 | 10 81 0A 00 09 00 00 00; | save $var=thermo4
01EA | 22 08 00 0D 04 00 00 00; | send.modbus $dev=tag4 $reg=13 $len=4
01EB | 03 02 D2 01 F0 49 02 00; | reuse #refresh_tag4 $sec=15
01EC | 04 01 00 00 00 00 00 00; | exit
01ED | 10 80 0A 00 09 00 00 00; | load $var=thermo4
01EE | 22 08 00 0D 04 00 00 00; | send.modbus $dev=tag4 $reg=13 $len=4
01EF | 03 02 D2 01 F0 49 02 00; | reuse #refresh_tag4 $sec=15
01F0 | 04 01 00 00 00 00 00 00; | exit
01F1 | 03 02 ED 01 00 00 00 00; | reuse #tag4_wakeup
01F2 | 01 01 00 00 60 EA 00 00; | wait $sec=6
01F3 | 26 08 00 19 02 00 00 00; | read.modbus $dev=tag4 $reg=25
01F4 | 10 81 0A 00 0F 00 00 00; | save $var=temp4
01F5 | 10 80 10 01 00 00 00 00; | load shift enum
01F6 | 22 FF 00 0B 08 00 00 00; | send.modbus $dev=server $reg=11 $len=8
01F7 | 04 01 00 00 00 00 00 00; | exit
01F8 | 01 01 00 00 20 4E 00 00; | wait $sec=2
01F9 | 10 80 0A 00 14 00 00 00; | load $var=room_empty
01FA | 07 01 FD 01 00 80 00 00; | if less than #+3 $hex=8000
01FB | 10 06 01 00 FF 7F FF FF; | math.and $relay=16
01FC | 10 01 0A 00 0F 00 00 00; | math.add $var=temp4
01FD | 22 08 00 19 02 00 00 00; | send.modbus $dev=tag4 $reg=25 $len=2
01FE | 04 01 00 00 00 00 00 00; | exit
01FF | 10 80 01 00 01 00 00 00; | load $hex=1
0200 | 01 01 80 05 00 00 00 00; | goto #set_last_action
0201 | 10 80 0A 00 0A 00 00 00; | load $var=thermo5
0202 | 10 06 01 00 AA AA 00 00; | math.and $hex=aaaa
0203 | 08 01 05 02 80 00 00 00; | if equal #+2 $hex=80
0204 | 10 08 01 00 01 00 00 00; | math.shiftr $dec=1
0205 | 22 09 00 0D 04 00 00 00; | send.modbus $dev=tag5 $reg=13 $len=4
0206 | 04 01 00 00 00 00 00 00; | exit
0207 | 20 FF 00 0D 04 01 00 00; | send.modbus $dev=server $reg=13 $hex=0401
0208 | 10 80 01 00 55 06 3F 00; | load $fan=fan1
0209 | 01 01 18 02 00 00 00 00; | goto #tag5_common
020A | 20 FF 00 0D 04 02 00 00; | send.modbus $dev=server $reg=13 $hex=0402
020B | 10 80 01 00 65 05 3F 00; | load $fan=fan2
020C | 01 01 18 02 00 00 00 00; | goto #tag5_common
020D | 20 FF 00 0D 04 03 00 00; | send.modbus $dev=server $reg=13 $hex=0403
020E | 10 80 01 00 56 05 3F 00; | load $fan=fan3
020F | 01 01 18 02 00 00 00 00; | goto #tag5_common
0210 | 20 FF 00 0D 04 04 00 00; | send.modbus $dev=server $reg=13 $hex=0404
0211 | 10 80 01 00 55 09 3F 00; | load $fan=auto
0212 | 01 01 18 02 00 00 00 00; | goto #tag5_common
0213 | 20 FF 00 0D 04 05 00 00; | send.modbus $dev=server $reg=13 $hex=0405
0214 | 10 80 01 00 95 05 3F 00; | load $fan=eco
0215 | 01 01 18 02 00 00 00 00; | goto #tag5_common
0216 | 20 FF 00 0D 04 06 00 00; | send.modbus $dev=server $reg=13 $hex=0406
0217 | 10 80 01 00 59 05 3F 00; | load $fan=off
0218 | 10 81 0A 00 0A 00 00 00; | save $var=thermo5
0219 | 22 09 00 0D 04 00 00 00; | send.modbus $dev=tag5 $reg=13 $len=4
021A | 03 02 01 02 F0 49 02 00; | reuse #refresh_tag5 $sec=15
021B | 04 01 00 00 00 00 00 00; | exit
021C | 10 80 0A 00 0A 00 00 00; | load $var=thermo5
021D | 22 09 00 0D 04 00 00 00; | send.modbus $dev=tag5 $reg=13 $len=4
021E | 03 02 01 02 F0 49 02 00; | reuse #refresh_tag5 $sec=15
021F | 04 01 00 00 00 00 00 00; | exit
0220 | 03 02 1C 02 00 00 00 00; | reuse #tag5_wakeup
0221 | 01 01 00 00 60 EA 00 00; | wait $sec=6
0222 | 26 09 00 19 02 00 00 00; | read.modbus $dev=tag5 $reg=25
0223 | 10 81 0A 00 10 00 00 00; | save $var=temp5
0224 | 10 80 10 01 00 00 00 00; | load shift enum
0225 | 22 FF 00 0B 08 00 00 00; | send.modbus $dev=server $reg=11 $len=8
0226 | 04 01 00 00 00 00 00 00; | exit
0227 | 01 01 00 00 20 4E 00 00; | wait $sec=2
0228 | 10 80 0A 00 14 00 00 00; | load $var=room_empty
0229 | 07 01 2C 02 00 80 00 00; | if less than #+3 $hex=8000
022A | 10 06 01 00 FF 7F FF FF; | math.and $relay=16
022B | 10 01 0A 00 10 00 00 00; | math.add $var=temp5
022C | 22 09 00 19 02 00 00 00; | send.modbus $dev=tag5 $reg=25 $len=2
022D | 04 01 00 00 00 00 00 00; | exit
022E | 10 80 01 00 01 00 00 00; | load $hex=1
022F | 01 01 80 05 00 00 00 00; | goto #set_last_action
0230 | 10 80 0A 00 0B 00 00 00; | load $var=thermo6
0231 | 10 06 01 00 AA AA 00 00; | math.and $hex=aaaa
0232 | 08 01 34 02 80 00 00 00; | if equal #+2 $hex=80
0233 | 10 08 01 00 01 00 00 00; | math.shiftr $dec=1
0234 | 22 0A 00 0D 04 00 00 00; | send.modbus $dev=tag6 $reg=13 $len=4
0235 | 04 01 00 00 00 00 00 00; | exit
0236 | 02 08 00 00 00 00 00 00; | rcu.read input
0237 | 10 05 01 00 02 00 00 00; | math.xor $bit=2
0238 | 09 01 5C 02 02 00 00 00; | if bit true #exit $bit=2
0239 | 20 FF 00 0D 05 01 00 00; | send.modbus $dev=server $reg=13 $hex=0501
023A | 10 80 01 00 55 06 3F 00; | load $fan=fan1
023B | 01 01 59 02 00 00 00 00; | goto #tag6_common
023C | 02 08 00 00 00 00 00 00; | rcu.read input
023D | 10 05 01 00 02 00 00 00; | math.xor $bit=2
023E | 09 01 5C 02 02 00 00 00; | if bit true #exit $bit=2
023F | 20 FF 00 0D 05 02 00 00; | send.modbus $dev=server $reg=13 $hex=0502
0240 | 10 80 01 00 65 05 3F 00; | load $fan=fan2
0241 | 01 01 59 02 00 00 00 00; | goto #tag6_common
0242 | 02 08 00 00 00 00 00 00; | rcu.read input
0243 | 10 05 01 00 02 00 00 00; | math.xor $bit=2
0244 | 09 01 5C 02 02 00 00 00; | if bit true #exit $bit=2
0245 | 20 FF 00 0D 05 03 00 00; | send.modbus $dev=server $reg=13 $hex=0503
0246 | 10 80 01 00 56 05 3F 00; | load $fan=fan3
0247 | 01 01 59 02 00 00 00 00; | goto #tag6_common
0248 | 02 08 00 00 00 00 00 00; | rcu.read input
0249 | 10 05 01 00 02 00 00 00; | math.xor $bit=2
024A | 09 01 5C 02 02 00 00 00; | if bit true #exit $bit=2
024B | 20 FF 00 0D 05 04 00 00; | send.modbus $dev=server $reg=13 $hex=0504
024C | 10 80 01 00 55 09 3F 00; | load $fan=auto
024D | 01 01 59 02 00 00 00 00; | goto #tag6_common
024E | 02 08 00 00 00 00 00 00; | rcu.read input
024F | 10 05 01 00 02 00 00 00; | math.xor $bit=2
0250 | 09 01 5C 02 02 00 00 00; | if bit true #exit $bit=2
0251 | 20 FF 00 0D 05 05 00 00; | send.modbus $dev=server $reg=13 $hex=0505
0252 | 10 80 01 00 95 05 3F 00; | load $fan=eco
0253 | 01 01 59 02 00 00 00 00; | goto #tag6_common
0254 | 02 08 00 00 00 00 00 00; | rcu.read input
0255 | 10 05 01 00 02 00 00 00; | math.xor $bit=2
0256 | 09 01 5C 02 02 00 00 00; | if bit true #exit $bit=2
0257 | 20 FF 00 0D 05 06 00 00; | send.modbus $dev=server $reg=13 $hex=0506
0258 | 10 80 01 00 59 05 3F 00; | load $fan=off
0259 | 10 81 0A 00 0B 00 00 00; | save $var=thermo6
025A | 22 0A 00 0D 04 00 00 00; | send.modbus $dev=tag6 $reg=13 $len=4
025B | 03 02 30 02 F0 49 02 00; | reuse #refresh_tag6 $sec=15
025C | 04 01 00 00 00 00 00 00; | exit
025D | 10 80 0A 00 0B 00 00 00; | load $var=thermo6
025E | 22 0A 00 0D 04 00 00 00; | send.modbus $dev=tag6 $reg=13 $len=4
025F | 03 02 30 02 F0 49 02 00; | reuse #refresh_tag6 $sec=15
0260 | 04 01 00 00 00 00 00 00; | exit
0261 | 02 08 00 00 00 00 00 00; | rcu.read input
0262 | 10 05 01 00 02 00 00 00; | math.xor $bit=2
0263 | 09 01 6A 02 02 00 00 00; | if bit true #exit $bit=2
0264 | 03 02 5D 02 00 00 00 00; | reuse #tag6_wakeup
0265 | 01 01 00 00 60 EA 00 00; | wait $sec=6
0266 | 26 0A 00 19 02 00 00 00; | read.modbus $dev=tag6 $reg=25
0267 | 10 81 0A 00 11 00 00 00; | save $var=temp6
0268 | 10 80 10 01 00 00 00 00; | load shift enum
0269 | 22 FF 00 0B 08 00 00 00; | send.modbus $dev=server $reg=11 $len=8
026A | 04 01 00 00 00 00 00 00; | exit
026B | 01 01 00 00 20 4E 00 00; | wait $sec=2
026C | 10 80 0A 00 14 00 00 00; | load $var=room_empty
026D | 07 01 70 02 00 80 00 00; | if less than #+3 $hex=8000
026E | 10 06 01 00 FF 7F FF FF; | math.and $relay=16
026F | 10 01 0A 00 11 00 00 00; | math.add $var=temp6
0270 | 22 0A 00 19 02 00 00 00; | send.modbus $dev=tag6 $reg=25 $len=2
0271 | 04 01 00 00 00 00 00 00; | exit
0272 | 10 80 01 00 01 00 00 00; | load $hex=1
0273 | 01 01 80 05 00 00 00 00; | goto #set_last_action
0274 | 10 80 01 00 07 00 00 00; | load $hex=7
0275 | 01 01 77 02 00 00 00 00; | goto #2
0276 | 10 80 01 00 00 00 00 00; | load $hex=0
0277 | 10 81 0A 00 16 00 00 00; | save $var=workflow
0278 | 22 FF 00 04 03 00 00 00; | send.modbus $dev=server $reg=4 $len=3
0279 | 03 02 2E 00 00 00 00 00; | reuse #refresh_idpg
027A | 22 02 00 06 02 00 00 00; | send.modbus $dev=2 $reg=6 $len=2
027B | 22 03 00 06 02 00 00 00; | send.modbus $dev=3 $reg=6 $len=2
027C | 03 02 DB 04 00 00 00 00; | reuse #dnd_relay
027D | 04 01 00 00 00 00 00 00; | exit
027E | 09 01 E1 04 00 00 00 01; | if bit true #pir1_close $bit=25
027F | 09 01 E7 04 00 00 00 02; | if bit true #pir2_close $bit=26
0280 | 09 01 ED 04 00 00 00 04; | if bit true #pir3_close $bit=27
0281 | 09 01 F3 04 00 00 00 08; | if bit true #pir4_close $bit=28
0282 | 09 01 F9 04 00 00 00 10; | if bit true #pir5_close $bit=29
0283 | 09 01 FF 04 00 00 00 20; | if bit true #pir6_close $bit=30
0284 | 09 01 E1 04 00 00 00 40; | if bit true #pir1_close $bit=31
0285 | 09 01 E7 04 00 00 00 80; | if bit true #pir2_close $bit=32
0286 | 04 01 00 00 00 00 00 00; | exit
0287 | 09 01 12 05 00 00 00 01; | if bit true #pir1_open $bit=25
0288 | 09 01 17 05 00 00 00 02; | if bit true #pir2_open $bit=26
0289 | 09 01 1C 05 00 00 00 04; | if bit true #pir3_open $bit=27
028A | 09 01 21 05 00 00 00 08; | if bit true #pir4_open $bit=28
028B | 09 01 26 05 00 00 00 10; | if bit true #pir5_open $bit=29
028C | 09 01 2B 05 00 00 00 20; | if bit true #pir6_open $bit=30
028D | 09 01 12 05 00 00 00 40; | if bit true #pir1_open $bit=31
028E | 09 01 17 05 00 00 00 80; | if bit true #pir2_open $bit=32
028F | 04 01 00 00 00 00 00 00; | exit
0290 | 10 81 0A 00 16 00 00 00; | save $var=workflow
0291 | 22 FF 00 04 03 00 00 00; | send.modbus $dev=server $reg=4 $len=3
0292 | 22 03 00 06 02 00 00 00; | send.modbus $dev=3 $reg=6 $len=2
0293 | 03 02 2E 00 00 00 00 00; | reuse #refresh_idpg
0294 | 03 02 DB 04 00 00 00 00; | reuse #dnd_relay
0295 | 04 01 00 00 00 00 00 00; | exit
0296 | 10 81 0A 00 16 00 00 00; | save $var=workflow
0297 | 22 FF 00 04 03 00 00 00; | send.modbus $dev=server $reg=4 $len=3
0298 | 22 02 00 06 02 00 00 00; | send.modbus $dev=2 $reg=6 $len=2
0299 | 03 02 2E 00 00 00 00 00; | reuse #refresh_idpg
029A | 03 02 DB 04 00 00 00 00; | reuse #dnd_relay
029B | 04 01 00 00 00 00 00 00; | exit
029C | 08 01 9E 02 00 00 00 00; | if equal #rcu2_restart $dec=0
029D | 04 01 00 00 00 00 00 00; | exit
029E | 20 FF 00 00 00 01 00 00; | send.modbus $dev=server $reg=0 $hex=1
029F | 04 01 00 00 00 00 00 00; | exit
02A0 | 10 81 0A 00 84 00 00 00; | save $var=rcu2_relays
02A1 | 04 01 00 00 00 00 00 00; | exit
02A2 | 10 81 0A 00 85 00 00 00; | save $var=rcu3_relays
02A3 | 04 01 00 00 00 00 00 00; | exit
02A4 | 08 01 0D 03 01 00 00 00; | if equal #bed1_on/off $dec=1
02A5 | 08 01 1A 03 02 00 00 00; | if equal #bed1_relax $dec=2
02A6 | 08 01 28 03 03 00 00 00; | if equal #bed1_night $dec=3
02A7 | 04 01 00 00 00 00 00 00; | exit
02A8 | 08 01 1A 03 01 00 00 00; | if equal #bed1_relax $dec=1
02A9 | 08 01 34 03 02 00 00 00; | if equal #bed1_light $dec=2
02AA | 04 01 00 00 00 00 00 00; | exit
02AB | 08 01 39 03 01 00 00 00; | if equal #bed2_on/off $dec=1
02AC | 08 01 46 03 02 00 00 00; | if equal #bed2_relax $dec=2
02AD | 08 01 54 03 03 00 00 00; | if equal #bed2_night $dec=3
02AE | 08 01 60 03 04 00 00 00; | if equal #bed2_light $dec=4
02AF | 04 01 00 00 00 00 00 00; | exit
02B0 | 08 01 65 03 01 00 00 00; | if equal #bed3_on/off $dec=1
02B1 | 08 01 7D 03 02 00 00 00; | if equal #bed3_relax $dec=2
02B2 | 08 01 8B 03 03 00 00 00; | if equal #bed3_night $dec=3
02B3 | 08 01 97 03 04 00 00 00; | if equal #bed3_light $dec=4
02B4 | 04 01 00 00 00 00 00 00; | exit
02B5 | 08 01 A9 03 01 00 00 00; | if equal #master_bed_relax $dec=1
02B6 | 08 01 C3 03 02 00 00 00; | if equal #master_bed_light $dec=2
02B7 | 04 01 00 00 00 00 00 00; | exit
02B8 | 08 01 BA 02 00 00 00 00; | if equal #rcu3_restart $dec=0
02B9 | 04 01 00 00 00 00 00 00; | exit
02BA | 20 FF 00 00 00 02 00 00; | send.modbus $dev=server $reg=0 $hex=2
02BB | 04 01 00 00 00 00 00 00; | exit
02BC | 08 01 9C 03 01 00 00 00; | if equal #master_bed_on/off $dec=1
02BD | 08 01 A9 03 02 00 00 00; | if equal #master_bed_relax $dec=2
02BE | 08 01 B7 03 03 00 00 00; | if equal #master_bed_night $dec=3
02BF | 08 01 C3 03 04 00 00 00; | if equal #master_bed_light $dec=4
02C0 | 04 01 00 00 00 00 00 00; | exit
02C1 | 08 01 C8 03 01 00 00 00; | if equal #bath1_relax $dec=1
02C2 | 08 01 D6 03 02 00 00 00; | if equal #bath1_master $dec=2
02C3 | 08 01 E2 03 03 00 00 00; | if equal #bath1_night $dec=3
02C4 | 04 01 00 00 00 00 00 00; | exit
02C5 | 08 01 E7 03 01 00 00 00; | if equal #bath2_relax $dec=1
02C6 | 08 01 F5 03 02 00 00 00; | if equal #bath2_master $dec=2
02C7 | 08 01 01 04 03 00 00 00; | if equal #bath2_night $dec=3
02C8 | 04 01 00 00 00 00 00 00; | exit
02C9 | 08 01 06 04 01 00 00 00; | if equal #bath3_relax $dec=1
02CA | 08 01 1F 04 02 00 00 00; | if equal #bath3_master $dec=2
02CB | 08 01 35 04 03 00 00 00; | if equal #bath3_night $dec=3
02CC | 04 01 00 00 00 00 00 00; | exit
02CD | 08 01 3A 04 01 00 00 00; | if equal #master_bath_relax $dec=1
02CE | 08 01 48 04 02 00 00 00; | if equal #master_bath_master $dec=2
02CF | 08 01 54 04 03 00 00 00; | if equal #master_bath_night $dec=3
02D0 | 04 01 00 00 00 00 00 00; | exit
02D1 | 08 01 59 04 01 00 00 00; | if equal #entrance_master $dec=1
02D2 | 08 01 71 04 02 00 00 00; | if equal #entrance_relax $dec=2
02D3 | 08 01 8A 04 03 00 00 00; | if equal #living_room $dec=3
02D4 | 08 01 A2 04 04 00 00 00; | if equal #lounge_light $dec=4
02D5 | 08 01 A7 04 05 00 00 00; | if equal #kitchen_light $dec=5
02D6 | 08 01 AC 04 06 00 00 00; | if equal #dining_light $dec=6
02D7 | 04 01 00 00 00 00 00 00; | exit
02D8 | 08 01 B1 04 01 00 00 00; | if equal #corridor_light $dec=1
02D9 | 08 01 8A 04 02 00 00 00; | if equal #living_room $dec=2
02DA | 08 01 B6 04 03 00 00 00; | if equal #storage1_light $dec=3
02DB | 08 01 BB 04 04 00 00 00; | if equal #storage2_light $dec=4
02DC | 04 01 00 00 00 00 00 00; | exit
02DD | 08 01 FF 04 01 00 00 00; | if equal #pir6_close $dec=1
02DE | 01 01 2B 05 00 00 00 00; | goto #pir6_open
02DF | 08 01 E1 02 00 00 00 00; | if equal #rcu4_restart $dec=0
02E0 | 04 01 00 00 00 00 00 00; | exit
02E1 | 20 FF 00 00 00 03 00 00; | send.modbus $dev=server $reg=0 $hex=3
02E2 | 04 01 00 00 00 00 00 00; | exit
02E3 | 22 FF 00 0D 04 00 00 00; | send.modbus $dev=server $reg=13 $len=4
02E4 | 04 01 00 00 00 00 00 00; | exit
02E5 | 10 80 01 01 06 00 00 00; | load shift $hex=6
02E6 | 22 FF 00 0B 08 00 00 00; | send.modbus $dev=server $reg=11 $len=8
02E7 | 04 01 00 00 00 00 00 00; | exit
02E8 | 10 80 01 01 06 00 00 00; | load shift $hex=6
02E9 | 22 FF 00 0A 08 00 00 00; | send.modbus $dev=server $reg=10 $len=8
02EA | 04 01 00 00 00 00 00 00; | exit
02EB | 10 80 01 01 71 00 00 00; | load shift $hex=71
02EC | 22 FF 00 FF 10 00 00 00; | send.modbus $dev=server $reg=255 $len=16
02ED | 04 01 00 00 00 00 00 00; | exit
02EE | 10 80 01 01 72 00 00 00; | load shift $hex=72
02EF | 22 FF 00 FF 10 00 00 00; | send.modbus $dev=server $reg=255 $len=16
02F0 | 04 01 00 00 00 00 00 00; | exit
02F1 | 10 80 01 01 73 00 00 00; | load shift $hex=73
02F2 | 22 FF 00 FF 10 00 00 00; | send.modbus $dev=server $reg=255 $len=16
02F3 | 04 01 00 00 00 00 00 00; | exit
02F4 | 10 80 01 01 74 00 00 00; | load shift $hex=74
02F5 | 22 FF 00 FF 10 00 00 00; | send.modbus $dev=server $reg=255 $len=16
02F6 | 04 01 00 00 00 00 00 00; | exit
02F7 | 10 80 0A 00 85 00 00 00; | load $var=rcu3_relays
02F8 | 10 05 01 00 00 80 00 00; | math.xor $relay=16
02F9 | 10 81 0A 00 85 00 00 00; | save $var=rcu3_relays
02FA | 22 03 00 07 02 00 00 00; | send.modbus $dev=3 $reg=7 $len=2
02FB | 04 01 00 00 00 00 00 00; | exit
02FC | 10 80 0A 00 85 00 00 00; | load $var=rcu3_relays
02FD | 10 05 01 00 00 40 00 00; | math.xor $relay=15
02FE | 10 81 0A 00 85 00 00 00; | save $var=rcu3_relays
02FF | 22 03 00 07 02 00 00 00; | send.modbus $dev=3 $reg=7 $len=2
0300 | 04 01 00 00 00 00 00 00; | exit
0301 | 10 80 0A 00 86 00 00 00; | load $var=rcu4_relays
0302 | 09 01 08 03 60 00 00 00; | if bit true #powder_room_off $relay=6,7
0303 | 10 80 0A 00 86 00 00 00; | load $var=rcu4_relays
0304 | 10 04 01 00 60 00 00 00; | math.or $relay=6,7
0305 | 10 81 0A 00 86 00 00 00; | save $var=rcu4_relays
0306 | 22 04 00 07 02 00 00 00; | send.modbus $dev=4 $reg=7 $len=2
0307 | 04 01 00 00 00 00 00 00; | exit
0308 | 10 80 0A 00 86 00 00 00; | load $var=rcu4_relays
0309 | 10 06 01 00 9F FF FF FF; | math.and $relay=6,7
030A | 10 81 0A 00 86 00 00 00; | save $var=rcu4_relays
030B | 22 04 00 07 02 00 00 00; | send.modbus $dev=4 $reg=7 $len=2
030C | 04 01 00 00 00 00 00 00; | exit
030D | 10 80 0A 00 86 00 00 00; | load $var=rcu4_relays
030E | 10 06 01 00 00 3F 00 00; | math.and $relay=1-8,15-32
030F | 05 01 15 03 00 3F 00 00; | if not equal #bed1_on $relay=9-14
0310 | 10 80 0A 00 86 00 00 00; | load $var=rcu4_relays
0311 | 10 06 01 00 FF C0 FF FF; | math.and $relay=9-14
0312 | 10 81 0A 00 86 00 00 00; | save $var=rcu4_relays
0313 | 22 04 00 07 02 00 00 00; | send.modbus $dev=4 $reg=7 $len=2
0314 | 04 01 00 00 00 00 00 00; | exit
0315 | 10 80 0A 00 86 00 00 00; | load $var=rcu4_relays
0316 | 10 04 01 00 00 3F 00 00; | math.or $relay=9-14
0317 | 10 81 0A 00 86 00 00 00; | save $var=rcu4_relays
0318 | 22 04 00 07 02 00 00 00; | send.modbus $dev=4 $reg=7 $len=2
0319 | 04 01 00 00 00 00 00 00; | exit
031A | 10 80 0A 00 86 00 00 00; | load $var=rcu4_relays
031B | 10 06 01 00 00 03 00 00; | math.and $relay=1-8,11-32
031C | 05 01 22 03 00 02 00 00; | if not equal #bed1_relax_on $relay=10
031D | 10 80 0A 00 86 00 00 00; | load $var=rcu4_relays
031E | 10 06 01 00 FF FC FF FF; | math.and $relay=9,10
031F | 10 81 0A 00 86 00 00 00; | save $var=rcu4_relays
0320 | 22 04 00 07 02 00 00 00; | send.modbus $dev=4 $reg=7 $len=2
0321 | 04 01 00 00 00 00 00 00; | exit
0322 | 10 80 0A 00 86 00 00 00; | load $var=rcu4_relays
0323 | 10 04 01 00 00 02 00 00; | math.or $relay=10
0324 | 10 06 01 00 FF FE FF FF; | math.and $relay=9
0325 | 10 81 0A 00 86 00 00 00; | save $var=rcu4_relays
0326 | 22 04 00 07 02 00 00 00; | send.modbus $dev=4 $reg=7 $len=2
0327 | 04 01 00 00 00 00 00 00; | exit
0328 | 10 80 0A 00 86 00 00 00; | load $var=rcu4_relays
0329 | 09 01 2F 03 00 22 00 00; | if bit true #bed1_night_off $relay=10,14
032A | 10 80 0A 00 86 00 00 00; | load $var=rcu4_relays
032B | 10 04 01 00 00 22 00 00; | math.or $relay=10,14
032C | 10 81 0A 00 86 00 00 00; | save $var=rcu4_relays
032D | 22 04 00 07 02 00 00 00; | send.modbus $dev=4 $reg=7 $len=2
032E | 04 01 00 00 00 00 00 00; | exit
032F | 10 80 0A 00 86 00 00 00; | load $var=rcu4_relays
0330 | 10 06 01 00 FF DD FF FF; | math.and $relay=10,14
0331 | 10 81 0A 00 86 00 00 00; | save $var=rcu4_relays
0332 | 22 04 00 07 02 00 00 00; | send.modbus $dev=4 $reg=7 $len=2
0333 | 04 01 00 00 00 00 00 00; | exit
0334 | 10 80 0A 00 86 00 00 00; | load $var=rcu4_relays
0335 | 10 05 01 00 00 01 00 00; | math.xor $relay=9
0336 | 10 81 0A 00 86 00 00 00; | save $var=rcu4_relays
0337 | 22 04 00 07 02 00 00 00; | send.modbus $dev=4 $reg=7 $len=2
0338 | 04 01 00 00 00 00 00 00; | exit
0339 | 10 80 0A 00 85 00 00 00; | load $var=rcu3_relays
033A | 10 06 01 00 40 3F 00 00; | math.and $relay=1-6,8,15-32
033B | 05 01 41 03 40 3F 00 00; | if not equal #bed2_on $relay=7,9-14
033C | 10 80 0A 00 85 00 00 00; | load $var=rcu3_relays
033D | 10 06 01 00 BF C0 FF FF; | math.and $relay=7,9-14
033E | 10 81 0A 00 85 00 00 00; | save $var=rcu3_relays
033F | 22 03 00 07 02 00 00 00; | send.modbus $dev=3 $reg=7 $len=2
0340 | 04 01 00 00 00 00 00 00; | exit
0341 | 10 80 0A 00 85 00 00 00; | load $var=rcu3_relays
0342 | 10 04 01 00 40 3F 00 00; | math.or $relay=7,9-14
0343 | 10 81 0A 00 85 00 00 00; | save $var=rcu3_relays
0344 | 22 03 00 07 02 00 00 00; | send.modbus $dev=3 $reg=7 $len=2
0345 | 04 01 00 00 00 00 00 00; | exit
0346 | 10 80 0A 00 85 00 00 00; | load $var=rcu3_relays
0347 | 10 06 01 00 40 01 00 00; | math.and $relay=1-6,8,10-32
0348 | 05 01 4E 03 00 01 00 00; | if not equal #bed2_relax_on $relay=9
0349 | 10 80 0A 00 85 00 00 00; | load $var=rcu3_relays
034A | 10 06 01 00 BF FE FF FF; | math.and $relay=7,9
034B | 10 81 0A 00 85 00 00 00; | save $var=rcu3_relays
034C | 22 03 00 07 02 00 00 00; | send.modbus $dev=3 $reg=7 $len=2
034D | 04 01 00 00 00 00 00 00; | exit
034E | 10 80 0A 00 85 00 00 00; | load $var=rcu3_relays
034F | 10 04 01 00 00 01 00 00; | math.or $relay=9
0350 | 10 06 01 00 BF FF FF FF; | math.and $relay=7
0351 | 10 81 0A 00 85 00 00 00; | save $var=rcu3_relays
0352 | 22 03 00 07 02 00 00 00; | send.modbus $dev=3 $reg=7 $len=2
0353 | 04 01 00 00 00 00 00 00; | exit
0354 | 10 80 0A 00 85 00 00 00; | load $var=rcu3_relays
0355 | 09 01 5B 03 00 21 00 00; | if bit true #bed2_night_off $relay=9,14
0356 | 10 80 0A 00 85 00 00 00; | load $var=rcu3_relays
0357 | 10 04 01 00 00 21 00 00; | math.or $relay=9,14
0358 | 10 81 0A 00 85 00 00 00; | save $var=rcu3_relays
0359 | 22 03 00 07 02 00 00 00; | send.modbus $dev=3 $reg=7 $len=2
035A | 04 01 00 00 00 00 00 00; | exit
035B | 10 80 0A 00 85 00 00 00; | load $var=rcu3_relays
035C | 10 06 01 00 FF DE FF FF; | math.and $relay=9,14
035D | 10 81 0A 00 85 00 00 00; | save $var=rcu3_relays
035E | 22 03 00 07 02 00 00 00; | send.modbus $dev=3 $reg=7 $len=2
035F | 04 01 00 00 00 00 00 00; | exit
0360 | 10 80 0A 00 85 00 00 00; | load $var=rcu3_relays
0361 | 10 05 01 00 40 00 00 00; | math.xor $relay=7
0362 | 10 81 0A 00 85 00 00 00; | save $var=rcu3_relays
0363 | 22 03 00 07 02 00 00 00; | send.modbus $dev=3 $reg=7 $len=2
0364 | 04 01 00 00 00 00 00 00; | exit
0365 | 10 80 0A 00 84 00 00 00; | load $var=rcu2_relays
0366 | 10 06 01 00 00 04 00 00; | math.and $relay=1-10,12-32
0367 | 05 01 74 03 00 04 00 00; | if not equal #bed3_on $relay=11
0368 | 10 80 0A 00 85 00 00 00; | load $var=rcu3_relays
0369 | 10 06 01 00 3F 00 00 00; | math.and $relay=7-32
036A | 05 01 74 03 3F 00 00 00; | if not equal #bed3_on $relay=1-6
036B | 10 80 0A 00 84 00 00 00; | load $var=rcu2_relays
036C | 10 06 01 00 FF FB FF FF; | math.and $relay=11
036D | 10 81 0A 00 84 00 00 00; | save $var=rcu2_relays
036E | 22 02 00 07 02 00 00 00; | send.modbus $dev=2 $reg=7 $len=2
036F | 10 80 0A 00 85 00 00 00; | load $var=rcu3_relays
0370 | 10 06 01 00 C0 FF FF FF; | math.and $relay=1-6
0371 | 10 81 0A 00 85 00 00 00; | save $var=rcu3_relays
0372 | 22 03 00 07 02 00 00 00; | send.modbus $dev=3 $reg=7 $len=2
0373 | 04 01 00 00 00 00 00 00; | exit
0374 | 10 80 0A 00 84 00 00 00; | load $var=rcu2_relays
0375 | 10 04 01 00 00 04 00 00; | math.or $relay=11
0376 | 10 81 0A 00 84 00 00 00; | save $var=rcu2_relays
0377 | 22 02 00 07 02 00 00 00; | send.modbus $dev=2 $reg=7 $len=2
0378 | 10 80 0A 00 85 00 00 00; | load $var=rcu3_relays
0379 | 10 04 01 00 3F 00 00 00; | math.or $relay=1-6
037A | 10 81 0A 00 85 00 00 00; | save $var=rcu3_relays
037B | 22 03 00 07 02 00 00 00; | send.modbus $dev=3 $reg=7 $len=2
037C | 04 01 00 00 00 00 00 00; | exit
037D | 10 80 0A 00 85 00 00 00; | load $var=rcu3_relays
037E | 10 06 01 00 03 00 00 00; | math.and $relay=3-32
037F | 05 01 85 03 02 00 00 00; | if not equal #bed3_relax_on $relay=2
0380 | 10 80 0A 00 85 00 00 00; | load $var=rcu3_relays
0381 | 10 06 01 00 FC FF FF FF; | math.and $relay=1,2
0382 | 10 81 0A 00 85 00 00 00; | save $var=rcu3_relays
0383 | 22 03 00 07 02 00 00 00; | send.modbus $dev=3 $reg=7 $len=2
0384 | 04 01 00 00 00 00 00 00; | exit
0385 | 10 80 0A 00 85 00 00 00; | load $var=rcu3_relays
0386 | 10 04 01 00 02 00 00 00; | math.or $relay=2
0387 | 10 06 01 00 FE FF FF FF; | math.and $relay=1
0388 | 10 81 0A 00 85 00 00 00; | save $var=rcu3_relays
0389 | 22 03 00 07 02 00 00 00; | send.modbus $dev=3 $reg=7 $len=2
038A | 04 01 00 00 00 00 00 00; | exit
038B | 10 80 0A 00 85 00 00 00; | load $var=rcu3_relays
038C | 09 01 92 03 22 00 00 00; | if bit true #bed3_night_off $relay=2,6
038D | 10 80 0A 00 85 00 00 00; | load $var=rcu3_relays
038E | 10 04 01 00 22 00 00 00; | math.or $relay=2,6
038F | 10 81 0A 00 85 00 00 00; | save $var=rcu3_relays
0390 | 22 03 00 07 02 00 00 00; | send.modbus $dev=3 $reg=7 $len=2
0391 | 04 01 00 00 00 00 00 00; | exit
0392 | 10 80 0A 00 85 00 00 00; | load $var=rcu3_relays
0393 | 10 06 01 00 DD FF FF FF; | math.and $relay=2,6
0394 | 10 81 0A 00 85 00 00 00; | save $var=rcu3_relays
0395 | 22 03 00 07 02 00 00 00; | send.modbus $dev=3 $reg=7 $len=2
0396 | 04 01 00 00 00 00 00 00; | exit
0397 | 10 80 0A 00 85 00 00 00; | load $var=rcu3_relays
0398 | 10 05 01 00 01 00 00 00; | math.xor $relay=1
0399 | 10 81 0A 00 85 00 00 00; | save $var=rcu3_relays
039A | 22 03 00 07 02 00 00 00; | send.modbus $dev=3 $reg=7 $len=2
039B | 04 01 00 00 00 00 00 00; | exit
039C | 10 80 0A 00 84 00 00 00; | load $var=rcu2_relays
039D | 10 06 01 00 F1 01 00 00; | math.and $relay=2-4,10-32
039E | 05 01 A4 03 F1 01 00 00; | if not equal #master_bed_on $relay=1,5-9
039F | 10 80 0A 00 84 00 00 00; | load $var=rcu2_relays
03A0 | 10 06 01 00 0E FE FF FF; | math.and $relay=1,5-9
03A1 | 10 81 0A 00 84 00 00 00; | save $var=rcu2_relays
03A2 | 22 02 00 07 02 00 00 00; | send.modbus $dev=2 $reg=7 $len=2
03A3 | 04 01 00 00 00 00 00 00; | exit
03A4 | 10 80 0A 00 84 00 00 00; | load $var=rcu2_relays
03A5 | 10 04 01 00 F1 01 00 00; | math.or $relay=1,5-9
03A6 | 10 81 0A 00 84 00 00 00; | save $var=rcu2_relays
03A7 | 22 02 00 07 02 00 00 00; | send.modbus $dev=2 $reg=7 $len=2
03A8 | 04 01 00 00 00 00 00 00; | exit
03A9 | 10 80 0A 00 84 00 00 00; | load $var=rcu2_relays
03AA | 10 06 01 00 01 01 00 00; | math.and $relay=2-8,10-32
03AB | 05 01 B1 03 01 00 00 00; | if not equal #master_bed_relax_on $relay=1
03AC | 10 80 0A 00 84 00 00 00; | load $var=rcu2_relays
03AD | 10 06 01 00 FE FE FF FF; | math.and $relay=1,9
03AE | 10 81 0A 00 84 00 00 00; | save $var=rcu2_relays
03AF | 22 02 00 07 02 00 00 00; | send.modbus $dev=2 $reg=7 $len=2
03B0 | 04 01 00 00 00 00 00 00; | exit
03B1 | 10 80 0A 00 84 00 00 00; | load $var=rcu2_relays
03B2 | 10 04 01 00 01 00 00 00; | math.or $relay=1
03B3 | 10 06 01 00 FF FE FF FF; | math.and $relay=9
03B4 | 10 81 0A 00 84 00 00 00; | save $var=rcu2_relays
03B5 | 22 02 00 07 02 00 00 00; | send.modbus $dev=2 $reg=7 $len=2
03B6 | 04 01 00 00 00 00 00 00; | exit
03B7 | 10 80 0A 00 84 00 00 00; | load $var=rcu2_relays
03B8 | 09 01 BE 03 81 00 00 00; | if bit true #master_bed_night_off $relay=1,8
03B9 | 10 80 0A 00 84 00 00 00; | load $var=rcu2_relays
03BA | 10 04 01 00 81 00 00 00; | math.or $relay=1,8
03BB | 10 81 0A 00 84 00 00 00; | save $var=rcu2_relays
03BC | 22 02 00 07 02 00 00 00; | send.modbus $dev=2 $reg=7 $len=2
03BD | 04 01 00 00 00 00 00 00; | exit
03BE | 10 80 0A 00 84 00 00 00; | load $var=rcu2_relays
03BF | 10 06 01 00 7E FF FF FF; | math.and $relay=1,8
03C0 | 10 81 0A 00 84 00 00 00; | save $var=rcu2_relays
03C1 | 22 02 00 07 02 00 00 00; | send.modbus $dev=2 $reg=7 $len=2
03C2 | 04 01 00 00 00 00 00 00; | exit
03C3 | 10 80 0A 00 84 00 00 00; | load $var=rcu2_relays
03C4 | 10 05 01 00 00 01 00 00; | math.xor $relay=9
03C5 | 10 81 0A 00 84 00 00 00; | save $var=rcu2_relays
03C6 | 22 02 00 07 02 00 00 00; | send.modbus $dev=2 $reg=7 $len=2
03C7 | 04 01 00 00 00 00 00 00; | exit
03C8 | 10 80 0A 00 86 00 00 00; | load $var=rcu4_relays
03C9 | 10 06 01 00 00 3C 00 00; | math.and $relay=1-10,15-32
03CA | 05 01 D0 03 00 04 00 00; | if not equal #bath1_relax_on $relay=11
03CB | 10 80 0A 00 86 00 00 00; | load $var=rcu4_relays
03CC | 10 06 01 00 FF C3 FF FF; | math.and $relay=11-14
03CD | 10 81 0A 00 86 00 00 00; | save $var=rcu4_relays
03CE | 22 04 00 07 02 00 00 00; | send.modbus $dev=4 $reg=7 $len=2
03CF | 04 01 00 00 00 00 00 00; | exit
03D0 | 10 80 0A 00 86 00 00 00; | load $var=rcu4_relays
03D1 | 10 04 01 00 00 04 00 00; | math.or $relay=11
03D2 | 10 06 01 00 FF C7 FF FF; | math.and $relay=12-14
03D3 | 10 81 0A 00 86 00 00 00; | save $var=rcu4_relays
03D4 | 22 04 00 07 02 00 00 00; | send.modbus $dev=4 $reg=7 $len=2
03D5 | 04 01 00 00 00 00 00 00; | exit
03D6 | 10 80 0A 00 86 00 00 00; | load $var=rcu4_relays
03D7 | 09 01 DD 03 00 1C 00 00; | if bit true #bath1_master_off $relay=11-13
03D8 | 10 80 0A 00 86 00 00 00; | load $var=rcu4_relays
03D9 | 10 04 01 00 00 1C 00 00; | math.or $relay=11-13
03DA | 10 81 0A 00 86 00 00 00; | save $var=rcu4_relays
03DB | 22 04 00 07 02 00 00 00; | send.modbus $dev=4 $reg=7 $len=2
03DC | 04 01 00 00 00 00 00 00; | exit
03DD | 10 80 0A 00 86 00 00 00; | load $var=rcu4_relays
03DE | 10 06 01 00 FF E3 FF FF; | math.and $relay=11-13
03DF | 10 81 0A 00 86 00 00 00; | save $var=rcu4_relays
03E0 | 22 04 00 07 02 00 00 00; | send.modbus $dev=4 $reg=7 $len=2
03E1 | 04 01 00 00 00 00 00 00; | exit
03E2 | 10 80 0A 00 86 00 00 00; | load $var=rcu4_relays
03E3 | 10 05 01 00 00 20 00 00; | math.xor $relay=14
03E4 | 10 81 0A 00 86 00 00 00; | save $var=rcu4_relays
03E5 | 22 04 00 07 02 00 00 00; | send.modbus $dev=4 $reg=7 $len=2
03E6 | 04 01 00 00 00 00 00 00; | exit
03E7 | 10 80 0A 00 85 00 00 00; | load $var=rcu3_relays
03E8 | 10 06 01 00 00 3E 00 00; | math.and $relay=1-9,15-32
03E9 | 05 01 EF 03 00 02 00 00; | if not equal #bath2_relax_on $relay=10
03EA | 10 80 0A 00 85 00 00 00; | load $var=rcu3_relays
03EB | 10 06 01 00 FF C1 FF FF; | math.and $relay=10-14
03EC | 10 81 0A 00 85 00 00 00; | save $var=rcu3_relays
03ED | 22 03 00 07 02 00 00 00; | send.modbus $dev=3 $reg=7 $len=2
03EE | 04 01 00 00 00 00 00 00; | exit
03EF | 10 80 0A 00 85 00 00 00; | load $var=rcu3_relays
03F0 | 10 04 01 00 00 02 00 00; | math.or $relay=10
03F1 | 10 06 01 00 FF C3 FF FF; | math.and $relay=11-14
03F2 | 10 81 0A 00 85 00 00 00; | save $var=rcu3_relays
03F3 | 22 03 00 07 02 00 00 00; | send.modbus $dev=3 $reg=7 $len=2
03F4 | 04 01 00 00 00 00 00 00; | exit
03F5 | 10 80 0A 00 85 00 00 00; | load $var=rcu3_relays
03F6 | 09 01 FC 03 00 1E 00 00; | if bit true #bath2_master_off $relay=10-13
03F7 | 10 80 0A 00 85 00 00 00; | load $var=rcu3_relays
03F8 | 10 04 01 00 00 1E 00 00; | math.or $relay=10-13
03F9 | 10 81 0A 00 85 00 00 00; | save $var=rcu3_relays
03FA | 22 03 00 07 02 00 00 00; | send.modbus $dev=3 $reg=7 $len=2
03FB | 04 01 00 00 00 00 00 00; | exit
03FC | 10 80 0A 00 85 00 00 00; | load $var=rcu3_relays
03FD | 10 06 01 00 FF E1 FF FF; | math.and $relay=10-13
03FE | 10 81 0A 00 85 00 00 00; | save $var=rcu3_relays
03FF | 22 03 00 07 02 00 00 00; | send.modbus $dev=3 $reg=7 $len=2
0400 | 04 01 00 00 00 00 00 00; | exit
0401 | 10 80 0A 00 85 00 00 00; | load $var=rcu3_relays
0402 | 10 05 01 00 00 20 00 00; | math.xor $relay=14
0403 | 10 81 0A 00 85 00 00 00; | save $var=rcu3_relays
0404 | 22 03 00 07 02 00 00 00; | send.modbus $dev=3 $reg=7 $len=2
0405 | 04 01 00 00 00 00 00 00; | exit
0406 | 10 80 0A 00 84 00 00 00; | load $var=rcu2_relays
0407 | 10 06 01 00 00 04 00 00; | math.and $relay=1-10,12-32
0408 | 05 01 15 04 00 00 00 00; | if not equal #bath3_relax_on $hex=0
0409 | 10 80 0A 00 85 00 00 00; | load $var=rcu3_relays
040A | 10 06 01 00 3C 00 00 00; | math.and $relay=1,2,7-32
040B | 05 01 15 04 04 00 00 00; | if not equal #bath3_relax_on $relay=3
040C | 10 80 0A 00 84 00 00 00; | load $var=rcu2_relays
040D | 10 06 01 00 FF FB FF FF; | math.and $relay=11
040E | 10 81 0A 00 84 00 00 00; | save $var=rcu2_relays
040F | 22 02 00 07 02 00 00 00; | send.modbus $dev=2 $reg=7 $len=2
0410 | 10 80 0A 00 85 00 00 00; | load $var=rcu3_relays
0411 | 10 06 01 00 C3 FF FF FF; | math.and $relay=3-6
0412 | 10 81 0A 00 85 00 00 00; | save $var=rcu3_relays
0413 | 22 03 00 07 02 00 00 00; | send.modbus $dev=3 $reg=7 $len=2
0414 | 04 01 00 00 00 00 00 00; | exit
0415 | 10 80 0A 00 84 00 00 00; | load $var=rcu2_relays
0416 | 10 06 01 00 FF FB FF FF; | math.and $relay=11
0417 | 10 81 0A 00 84 00 00 00; | save $var=rcu2_relays
0418 | 22 02 00 07 02 00 00 00; | send.modbus $dev=2 $reg=7 $len=2
0419 | 10 80 0A 00 85 00 00 00; | load $var=rcu3_relays
041A | 10 04 01 00 04 00 00 00; | math.or $relay=3
041B | 10 06 01 00 C7 FF FF FF; | math.and $relay=4-6
041C | 10 81 0A 00 85 00 00 00; | save $var=rcu3_relays
041D | 22 03 00 07 02 00 00 00; | send.modbus $dev=3 $reg=7 $len=2
041E | 04 01 00 00 00 00 00 00; | exit
041F | 10 80 0A 00 84 00 00 00; | load $var=rcu2_relays
0420 | 09 01 2C 04 00 04 00 00; | if bit true #bath3_master_off $relay=11
0421 | 10 80 0A 00 85 00 00 00; | load $var=rcu3_relays
0422 | 09 01 2C 04 1C 00 00 00; | if bit true #bath3_master_off $relay=3-5
0423 | 10 80 0A 00 84 00 00 00; | load $var=rcu2_relays
0424 | 10 04 01 00 00 04 00 00; | math.or $relay=11
0425 | 10 81 0A 00 84 00 00 00; | save $var=rcu2_relays
0426 | 22 02 00 07 02 00 00 00; | send.modbus $dev=2 $reg=7 $len=2
0427 | 10 80 0A 00 85 00 00 00; | load $var=rcu3_relays
0428 | 10 04 01 00 1C 00 00 00; | math.or $relay=3-5
0429 | 10 81 0A 00 85 00 00 00; | save $var=rcu3_relays
042A | 22 03 00 07 02 00 00 00; | send.modbus $dev=3 $reg=7 $len=2
042B | 04 01 00 00 00 00 00 00; | exit
042C | 10 80 0A 00 84 00 00 00; | load $var=rcu2_relays
042D | 10 06 01 00 FF FB FF FF; | math.and $relay=11
042E | 10 81 0A 00 84 00 00 00; | save $var=rcu2_relays
042F | 22 02 00 07 02 00 00 00; | send.modbus $dev=2 $reg=7 $len=2
0430 | 10 80 0A 00 85 00 00 00; | load $var=rcu3_relays
0431 | 10 06 01 00 E3 FF FF FF; | math.and $relay=3-5
0432 | 10 81 0A 00 85 00 00 00; | save $var=rcu3_relays
0433 | 22 03 00 07 02 00 00 00; | send.modbus $dev=3 $reg=7 $len=2
0434 | 04 01 00 00 00 00 00 00; | exit
0435 | 10 80 0A 00 85 00 00 00; | load $var=rcu3_relays
0436 | 10 05 01 00 20 00 00 00; | math.xor $relay=6
0437 | 10 81 0A 00 85 00 00 00; | save $var=rcu3_relays
0438 | 22 03 00 07 02 00 00 00; | send.modbus $dev=3 $reg=7 $len=2
0439 | 04 01 00 00 00 00 00 00; | exit
043A | 10 80 0A 00 84 00 00 00; | load $var=rcu2_relays
043B | 10 06 01 00 F0 00 00 00; | math.and $relay=1-4,9-32
043C | 05 01 42 04 10 00 00 00; | if not equal #master_bath_relax_on $relay=5
043D | 10 80 0A 00 84 00 00 00; | load $var=rcu2_relays
043E | 10 06 01 00 0F FF FF FF; | math.and $relay=5-8
043F | 10 81 0A 00 84 00 00 00; | save $var=rcu2_relays
0440 | 22 02 00 07 02 00 00 00; | send.modbus $dev=2 $reg=7 $len=2
0441 | 04 01 00 00 00 00 00 00; | exit
0442 | 10 80 0A 00 84 00 00 00; | load $var=rcu2_relays
0443 | 10 04 01 00 10 00 00 00; | math.or $relay=5
0444 | 10 06 01 00 1F FF FF FF; | math.and $relay=6-8
0445 | 10 81 0A 00 84 00 00 00; | save $var=rcu2_relays
0446 | 22 02 00 07 02 00 00 00; | send.modbus $dev=2 $reg=7 $len=2
0447 | 04 01 00 00 00 00 00 00; | exit
0448 | 10 80 0A 00 84 00 00 00; | load $var=rcu2_relays
0449 | 09 01 4F 04 70 00 00 00; | if bit true #master_bath_master_off $relay=5-7
044A | 10 80 0A 00 84 00 00 00; | load $var=rcu2_relays
044B | 10 04 01 00 70 00 00 00; | math.or $relay=5-7
044C | 10 81 0A 00 84 00 00 00; | save $var=rcu2_relays
044D | 22 02 00 07 02 00 00 00; | send.modbus $dev=2 $reg=7 $len=2
044E | 04 01 00 00 00 00 00 00; | exit
044F | 10 80 0A 00 84 00 00 00; | load $var=rcu2_relays
0450 | 10 06 01 00 8F FF FF FF; | math.and $relay=5-7
0451 | 10 81 0A 00 84 00 00 00; | save $var=rcu2_relays
0452 | 22 02 00 07 02 00 00 00; | send.modbus $dev=2 $reg=7 $len=2
0453 | 04 01 00 00 00 00 00 00; | exit
0454 | 10 80 0A 00 84 00 00 00; | load $var=rcu2_relays
0455 | 10 05 01 00 80 00 00 00; | math.xor $relay=8
0456 | 10 81 0A 00 84 00 00 00; | save $var=rcu2_relays
0457 | 22 02 00 07 02 00 00 00; | send.modbus $dev=2 $reg=7 $len=2
0458 | 04 01 00 00 00 00 00 00; | exit
0459 | 10 80 0A 00 84 00 00 00; | load $var=rcu2_relays
045A | 10 06 01 00 00 30 00 00; | math.and $relay=1-12,15-32
045B | 05 01 68 04 00 30 00 00; | if not equal #entrance_master_on $relay=13,14
045C | 10 80 0A 00 86 00 00 00; | load $var=rcu4_relays
045D | 10 06 01 00 18 C0 00 00; | math.and $relay=1-3,6-14,17-32
045E | 05 01 68 04 18 C0 00 00; | if not equal #entrance_master_on $relay=4,5,15,16
045F | 10 80 0A 00 84 00 00 00; | load $var=rcu2_relays
0460 | 10 06 01 00 FF CF FF FF; | math.and $relay=13,14
0461 | 10 81 0A 00 84 00 00 00; | save $var=rcu2_relays
0462 | 22 02 00 07 02 00 00 00; | send.modbus $dev=2 $reg=7 $len=2
0463 | 10 80 0A 00 86 00 00 00; | load $var=rcu4_relays
0464 | 10 06 01 00 E7 3F FF FF; | math.and $relay=4,5,15,16
0465 | 10 81 0A 00 86 00 00 00; | save $var=rcu4_relays
0466 | 22 04 00 07 02 00 00 00; | send.modbus $dev=4 $reg=7 $len=2
0467 | 04 01 00 00 00 00 00 00; | exit
0468 | 10 80 0A 00 84 00 00 00; | load $var=rcu2_relays
0469 | 10 04 01 00 00 30 00 00; | math.or $relay=13,14
046A | 10 81 0A 00 84 00 00 00; | save $var=rcu2_relays
046B | 22 02 00 07 02 00 00 00; | send.modbus $dev=2 $reg=7 $len=2
046C | 10 80 0A 00 86 00 00 00; | load $var=rcu4_relays
046D | 10 04 01 00 18 C0 00 00; | math.or $relay=4,5,15,16
046E | 10 81 0A 00 86 00 00 00; | save $var=rcu4_relays
046F | 22 04 00 07 02 00 00 00; | send.modbus $dev=4 $reg=7 $len=2
0470 | 04 01 00 00 00 00 00 00; | exit
0471 | 10 80 0A 00 84 00 00 00; | load $var=rcu2_relays
0472 | 10 06 01 00 00 10 00 00; | math.and $relay=1-12,14-32
0473 | 05 01 80 04 00 10 00 00; | if not equal #entrance_relax_on $relay=13
0474 | 10 80 0A 00 86 00 00 00; | load $var=rcu4_relays
0475 | 10 06 01 00 18 C0 00 00; | math.and $relay=1-3,6-14,17-32
0476 | 05 01 80 04 00 80 00 00; | if not equal #entrance_relax_on $relay=16
0477 | 10 80 0A 00 84 00 00 00; | load $var=rcu2_relays
0478 | 10 06 01 00 FF EF FF FF; | math.and $relay=13
0479 | 10 81 0A 00 84 00 00 00; | save $var=rcu2_relays
047A | 22 02 00 07 02 00 00 00; | send.modbus $dev=2 $reg=7 $len=2
047B | 10 80 0A 00 86 00 00 00; | load $var=rcu4_relays
047C | 10 06 01 00 E7 3F FF FF; | math.and $relay=4,5,15,16
047D | 10 81 0A 00 86 00 00 00; | save $var=rcu4_relays
047E | 22 04 00 07 02 00 00 00; | send.modbus $dev=4 $reg=7 $len=2
047F | 04 01 00 00 00 00 00 00; | exit
0480 | 10 80 0A 00 84 00 00 00; | load $var=rcu2_relays
0481 | 10 04 01 00 00 10 00 00; | math.or $relay=13
0482 | 10 81 0A 00 84 00 00 00; | save $var=rcu2_relays
0483 | 22 02 00 07 02 00 00 00; | send.modbus $dev=2 $reg=7 $len=2
0484 | 10 80 0A 00 86 00 00 00; | load $var=rcu4_relays
0485 | 10 04 01 00 00 80 00 00; | math.or $relay=16
0486 | 10 06 01 00 E7 BF FF FF; | math.and $relay=4,5,15
0487 | 10 81 0A 00 86 00 00 00; | save $var=rcu4_relays
0488 | 22 04 00 07 02 00 00 00; | send.modbus $dev=4 $reg=7 $len=2
0489 | 04 01 00 00 00 00 00 00; | exit
048A | 10 80 0A 00 84 00 00 00; | load $var=rcu2_relays
048B | 10 06 01 00 00 30 00 00; | math.and $relay=1-12,15-32
048C | 05 01 99 04 00 30 00 00; | if not equal #living_room_on $relay=13,14
048D | 10 80 0A 00 86 00 00 00; | load $var=rcu4_relays
048E | 10 06 01 00 08 C0 00 00; | math.and $relay=1-3,5-14,17-32
048F | 05 01 99 04 08 C0 00 00; | if not equal #living_room_on $relay=4,15,16
0490 | 10 80 0A 00 84 00 00 00; | load $var=rcu2_relays
0491 | 10 06 01 00 FF CF FF FF; | math.and $relay=13,14
0492 | 10 81 0A 00 84 00 00 00; | save $var=rcu2_relays
0493 | 22 02 00 07 02 00 00 00; | send.modbus $dev=2 $reg=7 $len=2
0494 | 10 80 0A 00 86 00 00 00; | load $var=rcu4_relays
0495 | 10 06 01 00 F7 3F FF FF; | math.and $relay=4,15,16
0496 | 10 81 0A 00 86 00 00 00; | save $var=rcu4_relays
0497 | 22 04 00 07 02 00 00 00; | send.modbus $dev=4 $reg=7 $len=2
0498 | 04 01 00 00 00 00 00 00; | exit
0499 | 10 80 0A 00 84 00 00 00; | load $var=rcu2_relays
049A | 10 04 01 00 00 30 00 00; | math.or $relay=13,14
049B | 10 81 0A 00 84 00 00 00; | save $var=rcu2_relays
049C | 22 02 00 07 02 00 00 00; | send.modbus $dev=2 $reg=7 $len=2
049D | 10 80 0A 00 86 00 00 00; | load $var=rcu4_relays
049E | 10 04 01 00 08 C0 00 00; | math.or $relay=4,15,16
049F | 10 81 0A 00 86 00 00 00; | save $var=rcu4_relays
04A0 | 22 04 00 07 02 00 00 00; | send.modbus $dev=4 $reg=7 $len=2
04A1 | 04 01 00 00 00 00 00 00; | exit
04A2 | 10 80 0A 00 86 00 00 00; | load $var=rcu4_relays
04A3 | 10 05 01 00 00 40 00 00; | math.xor $relay=15
04A4 | 10 81 0A 00 86 00 00 00; | save $var=rcu4_relays
04A5 | 22 04 00 07 02 00 00 00; | send.modbus $dev=4 $reg=7 $len=2
04A6 | 04 01 00 00 00 00 00 00; | exit
04A7 | 10 80 0A 00 86 00 00 00; | load $var=rcu4_relays
04A8 | 10 05 01 00 10 00 00 00; | math.xor $relay=5
04A9 | 10 81 0A 00 86 00 00 00; | save $var=rcu4_relays
04AA | 22 04 00 07 02 00 00 00; | send.modbus $dev=4 $reg=7 $len=2
04AB | 04 01 00 00 00 00 00 00; | exit
04AC | 10 80 0A 00 86 00 00 00; | load $var=rcu4_relays
04AD | 10 05 01 00 00 80 00 00; | math.xor $relay=16
04AE | 10 81 0A 00 86 00 00 00; | save $var=rcu4_relays
04AF | 22 04 00 07 02 00 00 00; | send.modbus $dev=4 $reg=7 $len=2
04B0 | 04 01 00 00 00 00 00 00; | exit
04B1 | 10 80 0A 00 84 00 00 00; | load $var=rcu2_relays
04B2 | 10 05 01 00 08 00 00 00; | math.xor $relay=4
04B3 | 10 81 0A 00 84 00 00 00; | save $var=rcu2_relays
04B4 | 22 02 00 07 02 00 00 00; | send.modbus $dev=2 $reg=7 $len=2
04B5 | 04 01 00 00 00 00 00 00; | exit
04B6 | 10 80 0A 00 84 00 00 00; | load $var=rcu2_relays
04B7 | 10 05 01 00 02 00 00 00; | math.xor $relay=2
04B8 | 10 81 0A 00 84 00 00 00; | save $var=rcu2_relays
04B9 | 22 02 00 07 02 00 00 00; | send.modbus $dev=2 $reg=7 $len=2
04BA | 04 01 00 00 00 00 00 00; | exit
04BB | 10 80 0A 00 84 00 00 00; | load $var=rcu2_relays
04BC | 10 05 01 00 04 00 00 00; | math.xor $relay=3
04BD | 10 81 0A 00 84 00 00 00; | save $var=rcu2_relays
04BE | 22 02 00 07 02 00 00 00; | send.modbus $dev=2 $reg=7 $len=2
04BF | 04 01 00 00 00 00 00 00; | exit
04C0 | 10 80 01 00 00 00 00 00; | load $dec=0
04C1 | 22 FE 00 0D 04 00 00 00; | send.modbus $dev=fe $reg=13 $len=4
04C2 | 04 01 00 00 00 00 00 00; | exit
04C3 | 03 02 F7 02 00 00 00 00; | reuse #maids_bathroom
04C4 | 10 80 01 00 00 04 00 00; | load $hex=400
04C5 | 22 FE 00 0D 04 00 00 00; | send.modbus $dev=fe $reg=13 $len=4
04C6 | 01 01 00 00 DC 05 00 00; | wait $sec=0.15
04C7 | 10 80 01 00 40 04 00 00; | load $hex=440
04C8 | 22 FE 00 0D 04 00 00 00; | send.modbus $dev=fe $reg=13 $len=4
04C9 | 03 02 C0 04 F0 49 02 00; | reuse #gsw02a_refresh $sec=15
04CA | 10 80 01 00 01 00 00 00; | load $hex=1
04CB | 01 01 80 05 00 00 00 00; | goto #set_last_action
04CC | 03 02 FC 02 00 00 00 00; | reuse #maids_bedroom
04CD | 10 80 01 00 40 00 00 00; | load $hex=40
04CE | 01 01 C5 04 00 00 00 00; | goto #gsw02a_btn_common
04CF | 10 80 01 00 00 00 00 00; | load $dec=0
04D0 | 22 FE 00 0D 04 00 00 00; | send.modbus $dev=fe $reg=13 $len=4
04D1 | 04 01 00 00 00 00 00 00; | exit
04D2 | 03 02 01 03 00 00 00 00; | reuse #powder_room
04D3 | 10 80 01 00 00 00 00 00; | load $hex=0
04D4 | 22 FE 00 0D 04 00 00 00; | send.modbus $dev=fe $reg=13 $len=4
04D5 | 01 01 00 00 DC 05 00 00; | wait $sec=0.15
04D6 | 10 80 01 00 00 01 00 00; | load $hex=100
04D7 | 22 FE 00 0D 04 00 00 00; | send.modbus $dev=fe $reg=13 $len=4
04D8 | 03 02 CF 04 F0 49 02 00; | reuse #gsw01_refresh $sec=15
04D9 | 10 80 01 00 01 00 00 00; | load $hex=1
04DA | 01 01 80 05 00 00 00 00; | goto #set_last_action
04DB | 10 80 0A 00 16 00 00 00; | load $var=workflow
04DC | 08 01 DF 04 07 00 00 00; | if equal #+3 $hex=7
04DD | 02 0A 01 00 00 10 00 00; | rcu.unset $relay=13
04DE | 04 01 00 00 00 00 00 00; | exit
04DF | 02 09 01 00 00 10 00 00; | rcu.set $relay=13
04E0 | 04 01 00 00 00 00 00 00; | exit
04E1 | 10 80 0A 00 82 00 00 00; | load $var=pir
04E2 | 10 04 01 00 01 00 00 00; | math.or $relay=1
04E3 | 10 81 0A 00 82 00 00 00; | save $var=pir
04E4 | 03 02 05 05 20 4E 00 00; | reuse #motion_relays $sec=2
04E5 | 10 80 01 00 02 00 00 00; | load $hex=2
04E6 | 01 01 80 05 00 00 00 00; | goto #set_last_action
04E7 | 10 80 0A 00 82 00 00 00; | load $var=pir
04E8 | 10 04 01 00 02 00 00 00; | math.or $relay=2
04E9 | 10 81 0A 00 82 00 00 00; | save $var=pir
04EA | 03 02 05 05 20 4E 00 00; | reuse #motion_relays $sec=2
04EB | 10 80 01 00 03 00 00 00; | load $hex=3
04EC | 01 01 80 05 00 00 00 00; | goto #set_last_action
04ED | 10 80 0A 00 82 00 00 00; | load $var=pir
04EE | 10 04 01 00 04 00 00 00; | math.or $relay=3
04EF | 10 81 0A 00 82 00 00 00; | save $var=pir
04F0 | 03 02 05 05 20 4E 00 00; | reuse #motion_relays $sec=2
04F1 | 10 80 01 00 04 00 00 00; | load $hex=4
04F2 | 01 01 80 05 00 00 00 00; | goto #set_last_action
04F3 | 10 80 0A 00 82 00 00 00; | load $var=pir
04F4 | 10 04 01 00 08 00 00 00; | math.or $relay=4
04F5 | 10 81 0A 00 82 00 00 00; | save $var=pir
04F6 | 03 02 05 05 20 4E 00 00; | reuse #motion_relays $sec=2
04F7 | 10 80 01 00 05 00 00 00; | load $hex=5
04F8 | 01 01 80 05 00 00 00 00; | goto #set_last_action
04F9 | 10 80 0A 00 82 00 00 00; | load $var=pir
04FA | 10 04 01 00 10 00 00 00; | math.or $relay=5
04FB | 10 81 0A 00 82 00 00 00; | save $var=pir
04FC | 03 02 05 05 20 4E 00 00; | reuse #motion_relays $sec=2
04FD | 10 80 01 00 06 00 00 00; | load $hex=6
04FE | 01 01 80 05 00 00 00 00; | goto #set_last_action
04FF | 10 80 0A 00 82 00 00 00; | load $var=pir
0500 | 10 04 01 00 20 00 00 00; | math.or $relay=6
0501 | 10 81 0A 00 82 00 00 00; | save $var=pir
0502 | 03 02 05 05 20 4E 00 00; | reuse #motion_relays $sec=2
0503 | 10 80 01 00 07 00 00 00; | load $hex=7
0504 | 01 01 80 05 00 00 00 00; | goto #set_last_action
0505 | 10 80 0A 00 84 00 00 00; | load $var=rcu2_relays
0506 | 09 01 0B 05 00 C2 00 00; | if bit true #+5 $relay=10,15,16
0507 | 10 80 0A 00 84 00 00 00; | load $var=rcu2_relays
0508 | 10 04 01 00 00 C2 00 00; | math.or $bit=10,15,16
0509 | 10 81 0A 00 84 00 00 00; | save $var=rcu2_relays
050A | 22 02 00 07 02 00 00 00; | send.modbus $dev=2 $reg=7 $len=2
050B | 10 80 0A 00 85 00 00 00; | load $var=rcu3_relays
050C | 09 01 11 05 80 00 00 00; | if bit true #exit $relay=8
050D | 10 80 0A 00 85 00 00 00; | load $var=rcu3_relays
050E | 10 04 01 00 80 00 00 00; | math.or $bit=8
050F | 10 81 0A 00 85 00 00 00; | save $var=rcu3_relays
0510 | 22 03 00 07 02 00 00 00; | send.modbus $dev=3 $reg=7 $len=2
0511 | 04 01 00 00 00 00 00 00; | exit
0512 | 10 80 0A 00 82 00 00 00; | load $var=pir
0513 | 10 06 01 00 FE FF FF FF; | math.and $relay=1
0514 | 10 81 0A 00 82 00 00 00; | save $var=pir
0515 | 03 03 30 05 40 0D 03 05; | reuse #check_exit_scene $sec=20 $dev=tag1
0516 | 04 01 00 00 00 00 00 00; | exit
0517 | 10 80 0A 00 82 00 00 00; | load $var=pir
0518 | 10 06 01 00 FD FF FF FF; | math.and $relay=2
0519 | 10 81 0A 00 82 00 00 00; | save $var=pir
051A | 03 03 30 05 40 0D 03 05; | reuse #check_exit_scene $sec=20 $dev=tag1
051B | 04 01 00 00 00 00 00 00; | exit
051C | 10 80 0A 00 82 00 00 00; | load $var=pir
051D | 10 06 01 00 FB FF FF FF; | math.and $relay=3
051E | 10 81 0A 00 82 00 00 00; | save $var=pir
051F | 03 03 30 05 40 0D 03 05; | reuse #check_exit_scene $sec=20 $dev=tag1
0520 | 04 01 00 00 00 00 00 00; | exit
0521 | 10 80 0A 00 82 00 00 00; | load $var=pir
0522 | 10 06 01 00 F7 FF FF FF; | math.and $relay=4
0523 | 10 81 0A 00 82 00 00 00; | save $var=pir
0524 | 03 03 30 05 40 0D 03 05; | reuse #check_exit_scene $sec=20 $dev=tag1
0525 | 04 01 00 00 00 00 00 00; | exit
0526 | 10 80 0A 00 82 00 00 00; | load $var=pir
0527 | 10 06 01 00 EF FF FF FF; | math.and $relay=5
0528 | 10 81 0A 00 82 00 00 00; | save $var=pir
0529 | 03 03 30 05 40 0D 03 05; | reuse #check_exit_scene $sec=20 $dev=tag1
052A | 04 01 00 00 00 00 00 00; | exit
052B | 10 80 0A 00 82 00 00 00; | load $var=pir
052C | 10 06 01 00 DF FF FF FF; | math.and $relay=6
052D | 10 81 0A 00 82 00 00 00; | save $var=pir
052E | 03 03 30 05 40 0D 03 05; | reuse #check_exit_scene $sec=20 $dev=tag1
052F | 04 01 00 00 00 00 00 00; | exit
0530 | 10 80 0A 00 80 00 00 00; | load $var=last_action
0531 | 09 01 37 05 FF 00 00 00; | if bit true #exit $hex=ff
0532 | 10 80 0A 00 82 00 00 00; | load $var=pir
0533 | 09 01 37 05 3F 00 00 00; | if bit true #exit $relay=1-6
0534 | 10 80 0A 00 15 00 00 00; | load $var=user
0535 | 08 01 38 05 10 00 00 00; | if equal #+3 $hex=10
0536 | 03 02 3A 05 00 A2 4A 04; | reuse #master_off_check $min=120
0537 | 04 01 00 00 00 00 00 00; | exit
0538 | 03 02 3A 05 C0 C6 2D 00; | reuse #master_off_check $min=5
0539 | 04 01 00 00 00 00 00 00; | exit
053A | 10 80 0A 00 82 00 00 00; | load $var=pir
053B | 09 01 7F 05 3F 00 00 00; | if bit true #exit $relay=1-6
053C | 10 80 0A 00 80 00 00 00; | load $var=last_action
053D | 09 01 7F 05 FF 00 00 00; | if bit true #exit $hex=ff
053E | 10 80 0A 00 15 00 00 00; | load $var=user
053F | 08 01 7F 05 00 00 00 00; | if equal #exit $dec=0
0540 | 10 80 01 00 00 C0 00 00; | load $relay=15,16
0541 | 22 02 00 07 02 00 00 00; | send.modbus $dev=2 $reg=7 $len=2
0542 | 10 80 01 00 00 00 00 00; | load $hex=0
0543 | 22 03 00 07 02 00 00 00; | send.modbus $dev=3 $reg=7 $len=2
0544 | 10 80 01 00 00 00 00 00; | load $hex=0
0545 | 22 04 00 07 02 00 00 00; | send.modbus $dev=4 $reg=7 $len=2
0546 | 10 80 01 00 00 00 00 00; | load $hex=0
0547 | 10 81 0A 00 15 00 00 00; | save $var=user
0548 | 22 02 00 05 02 00 00 00; | send.modbus $dev=2 $reg=5 $len=2
0549 | 22 03 00 05 02 00 00 00; | send.modbus $dev=3 $reg=5 $len=2
054A | 22 04 00 05 02 00 00 00; | send.modbus $dev=4 $reg=5 $len=2
054B | 22 FF 00 03 10 00 00 00; | send.modbus $dev=server $reg=3 $len=16
054C | 10 80 01 00 01 00 00 00; | load $hex=01
054D | 10 81 0A 00 12 00 00 00; | save $var=season
054E | 03 03 74 01 00 00 00 06; | reuse #refresh_tag2 $dev=tag2
054F | 10 80 0A 00 14 00 00 00; | load $var=room_empty
0550 | 07 01 53 05 00 80 00 00; | if less than #+3 $hex=8000
0551 | 10 06 01 00 FF 7F FF FF; | math.and $relay=16
0552 | 10 01 0A 00 0D 00 00 00; | math.add $var=temp2
0553 | 22 06 00 19 02 00 00 00; | send.modbus $dev=tag2 $reg=25 $len=2
0554 | 03 03 A3 01 00 00 00 07; | reuse #refresh_tag3 $dev=tag3
0555 | 10 80 0A 00 14 00 00 00; | load $var=room_empty
0556 | 07 01 59 05 00 80 00 00; | if less than #+3 $hex=8000
0557 | 10 06 01 00 FF 7F FF FF; | math.and $relay=16
0558 | 10 01 0A 00 0E 00 00 00; | math.add $var=temp3
0559 | 22 07 00 19 02 00 00 00; | send.modbus $dev=tag3 $reg=25 $len=2
055A | 03 03 D2 01 00 00 00 08; | reuse #refresh_tag4 $dev=tag4
055B | 10 80 0A 00 14 00 00 00; | load $var=room_empty
055C | 07 01 5F 05 00 80 00 00; | if less than #+3 $hex=8000
055D | 10 06 01 00 FF 7F FF FF; | math.and $relay=16
055E | 10 01 0A 00 0F 00 00 00; | math.add $var=temp4
055F | 22 08 00 19 02 00 00 00; | send.modbus $dev=tag4 $reg=25 $len=2
0560 | 03 03 01 02 00 00 00 09; | reuse #refresh_tag5 $dev=tag5
0561 | 10 80 0A 00 14 00 00 00; | load $var=room_empty
0562 | 07 01 65 05 00 80 00 00; | if less than #+3 $hex=8000
0563 | 10 06 01 00 FF 7F FF FF; | math.and $relay=16
0564 | 10 01 0A 00 10 00 00 00; | math.add $var=temp5
0565 | 22 09 00 19 02 00 00 00; | send.modbus $dev=tag5 $reg=25 $len=2
0566 | 01 01 00 00 20 4E 00 00; | wait $sec=2
0567 | 10 80 01 00 80 00 00 00; | load $hex=80
0568 | 22 06 00 0D 04 00 00 00; | send.modbus $dev=tag2 $reg=13 $len=4
0569 | 22 07 00 0D 04 00 00 00; | send.modbus $dev=tag3 $reg=13 $len=4
056A | 22 08 00 0D 04 00 00 00; | send.modbus $dev=tag4 $reg=13 $len=4
056B | 22 09 00 0D 04 00 00 00; | send.modbus $dev=tag5 $reg=13 $len=4
056C | 02 08 00 00 00 00 00 00; | rcu.read input
056D | 10 05 01 00 02 00 00 00; | math.xor $bit=2
056E | 09 01 7F 05 02 00 00 00; | if bit true #exit $bit=2
056F | 03 03 F9 00 00 00 00 05; | reuse #refresh_tag1 $dev=tag1
0570 | 10 80 0A 00 14 00 00 00; | load $var=room_empty
0571 | 07 01 74 05 00 80 00 00; | if less than #+3 $hex=8000
0572 | 10 06 01 00 FF 7F FF FF; | math.and $relay=16
0573 | 10 01 0A 00 0C 00 00 00; | math.add $var=temp1
0574 | 22 05 00 19 02 00 00 00; | send.modbus $dev=tag1 $reg=25 $len=2
0575 | 03 03 30 02 00 00 00 0A; | reuse #refresh_tag6 $dev=tag6
0576 | 10 80 0A 00 14 00 00 00; | load $var=room_empty
0577 | 07 01 7A 05 00 80 00 00; | if less than #+3 $hex=8000
0578 | 10 06 01 00 FF 7F FF FF; | math.and $relay=16
0579 | 10 01 0A 00 11 00 00 00; | math.add $var=temp6
057A | 22 0A 00 19 02 00 00 00; | send.modbus $dev=tag6 $reg=25 $len=2
057B | 01 01 00 00 20 4E 00 00; | wait $sec=2
057C | 10 80 01 00 80 00 00 00; | load $hex=80
057D | 22 05 00 0D 04 00 00 00; | send.modbus $dev=tag1 $reg=13 $len=4
057E | 22 0A 00 0D 04 00 00 00; | send.modbus $dev=tag6 $reg=13 $len=4
057F | 04 01 00 00 00 00 00 00; | exit
0580 | 10 03 01 00 00 01 00 00; | math.mul $hex=100
0581 | 10 04 0A 00 80 00 00 00; | math.or $var=last_action
0582 | 10 81 0A 00 80 00 00 00; | save $var=last_action
0583 | 10 06 01 00 FF 00 00 00; | math.and $hex=ff
0584 | 05 01 8B 05 00 00 00 00; | if not equal #skip_notify_interrupt $hex=0
0585 | 10 80 0A 00 15 00 00 00; | load $var=user
0586 | 08 01 8B 05 00 00 00 00; | if equal #skip_notify_interrupt $hex=0
0587 | 10 80 0A 00 80 00 00 00; | load $var=last_action
0588 | 10 09 01 00 00 01 00 00; | math.div $hex=100
0589 | 08 01 8B 05 00 00 00 00; | if equal #skip_notify_interrupt $hex=0
058A | 22 FF 00 11 10 00 00 00; | send.modbus $dev=server $reg=17 $len=16
058B | 10 80 0A 00 80 00 00 00; | load $var=last_action
058C | 10 09 01 00 00 01 00 00; | math.div $hex=100
058D | 10 81 0A 00 80 00 00 00; | save $var=last_action
058E | 10 80 0A 00 15 00 00 00; | load $var=user
058F | 09 01 91 05 FF 00 00 00; | if bit true #exit $hex=ff
0590 | 01 01 92 05 00 00 00 00; | goto #motion_detect_from_inside
0591 | 04 01 00 00 00 00 00 00; | exit
0592 | 10 80 0A 00 81 00 00 00; | load $var=temp_user
0593 | 10 81 0A 00 15 00 00 00; | save $var=user
0594 | 22 02 00 05 02 00 00 00; | send.modbus $dev=2 $reg=5 $len=2
0595 | 01 01 00 00 DC 05 00 00; | wait $sec=0.15
0596 | 22 03 00 05 02 00 00 00; | send.modbus $dev=3 $reg=5 $len=2
0597 | 01 01 00 00 DC 05 00 00; | wait $sec=0.15
0598 | 22 04 00 05 02 00 00 00; | send.modbus $dev=4 $reg=5 $len=2
0599 | 10 80 0A 00 80 00 00 00; | load $var=last_action
059A | 22 FF 00 02 10 00 00 00; | send.modbus $dev=server $reg=2 $len=16
059B | 10 80 01 00 11 00 00 00; | load $hex=11
059C | 10 81 0A 00 12 00 00 00; | save $var=season
059D | 10 80 0A 00 84 00 00 00; | load $var=rcu2_relays
059E | 22 02 00 07 02 00 00 00; | send.modbus $dev=2 $reg=7 $len=2
059F | 10 80 0A 00 85 00 00 00; | load $var=rcu3_relays
05A0 | 22 03 00 07 02 00 00 00; | send.modbus $dev=3 $reg=7 $len=2
05A1 | 10 80 0A 00 86 00 00 00; | load $var=rcu4_relays
05A2 | 22 04 00 07 02 00 00 00; | send.modbus $dev=4 $reg=7 $len=2
05A3 | 01 01 79 00 00 00 00 00; | goto #tag_conditional_check_with_user
05A4 | 04 01 00 00 00 00 00 00; | exit
05A5 | 10 80 0A 00 84 00 00 00; | load $var=rcu2_relays
05A6 | 22 02 00 07 02 00 00 00; | send.modbus $dev=2 $reg=7 $len=2
05A7 | 10 80 0A 00 85 00 00 00; | load $var=rcu3_relays
05A8 | 22 03 00 07 02 00 00 00; | send.modbus $dev=3 $reg=7 $len=2
05A9 | 10 80 0A 00 86 00 00 00; | load $var=rcu4_relays
05AA | 22 04 00 07 02 00 00 00; | send.modbus $dev=4 $reg=7 $len=2
05AB | 03 02 DB 04 00 00 00 00; | reuse #dnd_relay
05AC | 04 01 00 00 00 00 00 00; | exit
05AD | 26 0D 00 03 02 00 00 00; | read.modbus $dev=13 $reg=3
05AE | 08 0A B2 05 89 00 00 00; | if equal goto #+4 $var=pt100_1_water_return
05AF | 10 81 0A 00 89 00 00 00; | save $var=pt100_1_water_return
05B0 | 10 80 01 01 11 00 00 00; | load shift $hex=11
05B1 | 22 FF 00 FF 10 00 00 00; | send.modbus $dev=server $reg=255 $len=16
05B2 | 01 01 00 00 E0 93 04 00; | wait $sec=30
05B3 | 26 0D 00 04 02 00 00 00; | read.modbus $dev=13 $reg=4
05B4 | 08 0A B8 05 8A 00 00 00; | if equal goto #+4 $var=pt100_1_water_supply
05B5 | 10 81 0A 00 8A 00 00 00; | save $var=pt100_1_water_supply
05B6 | 10 80 01 01 12 00 00 00; | load shift $hex=12
05B7 | 22 FF 00 FF 10 00 00 00; | send.modbus $dev=server $reg=255 $len=16
05B8 | 01 01 00 00 E0 93 04 00; | wait $sec=30
05B9 | 26 0D 00 05 02 00 00 00; | read.modbus $dev=13 $reg=5
05BA | 08 0A BE 05 8B 00 00 00; | if equal goto #+4 $var=pt100_1_air_return
05BB | 10 81 0A 00 8B 00 00 00; | save $var=pt100_1_air_return
05BC | 10 80 01 01 13 00 00 00; | load shift $hex=13
05BD | 22 FF 00 FF 10 00 00 00; | send.modbus $dev=server $reg=255 $len=16
05BE | 01 01 00 00 E0 93 04 00; | wait $sec=30
05BF | 26 0D 00 06 02 00 00 00; | read.modbus $dev=13 $reg=6
05C0 | 08 0A C4 05 8C 00 00 00; | if equal goto #+4 $var=pt100_1_air_supply
05C1 | 10 81 0A 00 8C 00 00 00; | save $var=pt100_1_air_supply
05C2 | 10 80 01 01 14 00 00 00; | load shift $hex=14
05C3 | 22 FF 00 FF 10 00 00 00; | send.modbus $dev=server $reg=255 $len=16
05C4 | 01 01 00 00 E0 93 04 00; | wait $sec=30
05C5 | 26 0E 00 03 02 00 00 00; | read.modbus $dev=14 $reg=3
05C6 | 08 0A CA 05 8D 00 00 00; | if equal goto #+4 $var=pt100_2_water_return
05C7 | 10 81 0A 00 8D 00 00 00; | save $var=pt100_2_water_return
05C8 | 10 80 01 01 21 00 00 00; | load shift $hex=21
05C9 | 22 FF 00 FF 10 00 00 00; | send.modbus $dev=server $reg=255 $len=16
05CA | 01 01 00 00 E0 93 04 00; | wait $sec=30
05CB | 26 0E 00 04 02 00 00 00; | read.modbus $dev=14 $reg=4
05CC | 08 0A D0 05 8E 00 00 00; | if equal goto #+4 $var=pt100_2_water_supply
05CD | 10 81 0A 00 8E 00 00 00; | save $var=pt100_2_water_supply
05CE | 10 80 01 01 22 00 00 00; | load shift $hex=22
05CF | 22 FF 00 FF 10 00 00 00; | send.modbus $dev=server $reg=255 $len=16
05D0 | 01 01 00 00 E0 93 04 00; | wait $sec=30
05D1 | 26 0E 00 05 02 00 00 00; | read.modbus $dev=14 $reg=5
05D2 | 08 0A D6 05 8F 00 00 00; | if equal goto #+4 $var=pt100_2_air_return
05D3 | 10 81 0A 00 8F 00 00 00; | save $var=pt100_2_air_return
05D4 | 10 80 01 01 23 00 00 00; | load shift $hex=23
05D5 | 22 FF 00 FF 10 00 00 00; | send.modbus $dev=server $reg=255 $len=16
05D6 | 01 01 00 00 E0 93 04 00; | wait $sec=30
05D7 | 26 0E 00 06 02 00 00 00; | read.modbus $dev=14 $reg=6
05D8 | 08 0A DC 05 90 00 00 00; | if equal goto #+4 $var=pt100_2_air_supply
05D9 | 10 81 0A 00 90 00 00 00; | save $var=pt100_2_air_supply
05DA | 10 80 01 01 24 00 00 00; | load shift $hex=24
05DB | 22 FF 00 FF 10 00 00 00; | send.modbus $dev=server $reg=255 $len=16
05DC | 01 01 00 00 E0 93 04 00; | wait $sec=30
05DD | 26 0F 00 03 02 00 00 00; | read.modbus $dev=15 $reg=3
05DE | 08 0A E2 05 91 00 00 00; | if equal goto #+4 $var=pt100_3_water_return
05DF | 10 81 0A 00 91 00 00 00; | save $var=pt100_3_water_return
05E0 | 10 80 01 01 31 00 00 00; | load shift $hex=31
05E1 | 22 FF 00 FF 10 00 00 00; | send.modbus $dev=server $reg=255 $len=16
05E2 | 01 01 00 00 E0 93 04 00; | wait $sec=30
05E3 | 26 0F 00 04 02 00 00 00; | read.modbus $dev=15 $reg=4
05E4 | 08 0A E8 05 92 00 00 00; | if equal goto #+4 $var=pt100_3_water_supply
05E5 | 10 81 0A 00 92 00 00 00; | save $var=pt100_3_water_supply
05E6 | 10 80 01 01 32 00 00 00; | load shift $hex=32
05E7 | 22 FF 00 FF 10 00 00 00; | send.modbus $dev=server $reg=255 $len=16
05E8 | 01 01 00 00 E0 93 04 00; | wait $sec=30
05E9 | 26 0F 00 05 02 00 00 00; | read.modbus $dev=15 $reg=5
05EA | 08 0A EE 05 93 00 00 00; | if equal goto #+4 $var=pt100_3_air_return
05EB | 10 81 0A 00 93 00 00 00; | save $var=pt100_3_air_return
05EC | 10 80 01 01 33 00 00 00; | load shift $hex=33
05ED | 22 FF 00 FF 10 00 00 00; | send.modbus $dev=server $reg=255 $len=16
05EE | 01 01 00 00 E0 93 04 00; | wait $sec=30
05EF | 26 0F 00 06 02 00 00 00; | read.modbus $dev=15 $reg=6
05F0 | 08 0A F4 05 94 00 00 00; | if equal goto #+4 $var=pt100_3_air_supply
05F1 | 10 81 0A 00 94 00 00 00; | save $var=pt100_3_air_supply
05F2 | 10 80 01 01 34 00 00 00; | load shift $hex=34
05F3 | 22 FF 00 FF 10 00 00 00; | send.modbus $dev=server $reg=255 $len=16
05F4 | 01 01 00 00 E0 93 04 00; | wait $sec=30
05F5 | 26 10 00 03 02 00 00 00; | read.modbus $dev=16 $reg=3
05F6 | 08 0A FA 05 95 00 00 00; | if equal goto #+4 $var=pt100_4_water_return
05F7 | 10 81 0A 00 95 00 00 00; | save $var=pt100_4_water_return
05F8 | 10 80 01 01 41 00 00 00; | load shift $hex=41
05F9 | 22 FF 00 FF 10 00 00 00; | send.modbus $dev=server $reg=255 $len=16
05FA | 01 01 00 00 E0 93 04 00; | wait $sec=30
05FB | 26 10 00 04 02 00 00 00; | read.modbus $dev=16 $reg=4
05FC | 08 0A 00 06 96 00 00 00; | if equal goto #+4 $var=pt100_4_water_supply
05FD | 10 81 0A 00 96 00 00 00; | save $var=pt100_4_water_supply
05FE | 10 80 01 01 42 00 00 00; | load shift $hex=42
05FF | 22 FF 00 FF 10 00 00 00; | send.modbus $dev=server $reg=255 $len=16
0600 | 01 01 00 00 E0 93 04 00; | wait $sec=30
0601 | 26 10 00 05 02 00 00 00; | read.modbus $dev=16 $reg=5
0602 | 08 0A 06 06 97 00 00 00; | if equal goto #+4 $var=pt100_4_air_return
0603 | 10 81 0A 00 97 00 00 00; | save $var=pt100_4_air_return
0604 | 10 80 01 01 43 00 00 00; | load shift $hex=43
0605 | 22 FF 00 FF 10 00 00 00; | send.modbus $dev=server $reg=255 $len=16
0606 | 01 01 00 00 E0 93 04 00; | wait $sec=30
0607 | 26 10 00 06 02 00 00 00; | read.modbus $dev=16 $reg=6
0608 | 08 0A 0C 06 98 00 00 00; | if equal goto #+4 $var=pt100_4_air_supply
0609 | 10 81 0A 00 98 00 00 00; | save $var=pt100_4_air_supply
060A | 10 80 01 01 44 00 00 00; | load shift $hex=44
060B | 22 FF 00 FF 10 00 00 00; | send.modbus $dev=server $reg=255 $len=16
060C | 01 01 00 00 E0 93 04 00; | wait $sec=30
060D | 26 11 00 03 02 00 00 00; | read.modbus $dev=17 $reg=3
060E | 08 0A 12 06 99 00 00 00; | if equal goto #+4 $var=pt100_5_water_return
060F | 10 81 0A 00 99 00 00 00; | save $var=pt100_5_water_return
0610 | 10 80 01 01 51 00 00 00; | load shift $hex=51
0611 | 22 FF 00 FF 10 00 00 00; | send.modbus $dev=server $reg=255 $len=16
0612 | 01 01 00 00 E0 93 04 00; | wait $sec=30
0613 | 26 11 00 04 02 00 00 00; | read.modbus $dev=17 $reg=4
0614 | 08 0A 18 06 9A 00 00 00; | if equal goto #+4 $var=pt100_5_water_supply
0615 | 10 81 0A 00 9A 00 00 00; | save $var=pt100_5_water_supply
0616 | 10 80 01 01 52 00 00 00; | load shift $hex=52
0617 | 22 FF 00 FF 10 00 00 00; | send.modbus $dev=server $reg=255 $len=16
0618 | 01 01 00 00 E0 93 04 00; | wait $sec=30
0619 | 26 11 00 05 02 00 00 00; | read.modbus $dev=17 $reg=5
061A | 08 0A 1E 06 9B 00 00 00; | if equal goto #+4 $var=pt100_5_air_return
061B | 10 81 0A 00 9B 00 00 00; | save $var=pt100_5_air_return
061C | 10 80 01 01 53 00 00 00; | load shift $hex=53
061D | 22 FF 00 FF 10 00 00 00; | send.modbus $dev=server $reg=255 $len=16
061E | 01 01 00 00 E0 93 04 00; | wait $sec=30
061F | 26 11 00 06 02 00 00 00; | read.modbus $dev=17 $reg=6
0620 | 08 0A 24 06 9C 00 00 00; | if equal goto #+4 $var=pt100_5_air_supply
0621 | 10 81 0A 00 9C 00 00 00; | save $var=pt100_5_air_supply
0622 | 10 80 01 01 54 00 00 00; | load shift $hex=54
0623 | 22 FF 00 FF 10 00 00 00; | send.modbus $dev=server $reg=255 $len=16
0624 | 01 01 00 00 E0 93 04 00; | wait $sec=30
0625 | 26 12 00 03 02 00 00 00; | read.modbus $dev=18 $reg=3
0626 | 08 0A 2A 06 9D 00 00 00; | if equal goto #+4 $var=pt100_6_water_return
0627 | 10 81 0A 00 9D 00 00 00; | save $var=pt100_6_water_return
0628 | 10 80 01 01 61 00 00 00; | load shift $hex=61
0629 | 22 FF 00 FF 10 00 00 00; | send.modbus $dev=server $reg=255 $len=16
062A | 01 01 00 00 E0 93 04 00; | wait $sec=30
062B | 26 12 00 04 02 00 00 00; | read.modbus $dev=18 $reg=4
062C | 08 0A 30 06 9E 00 00 00; | if equal goto #+4 $var=pt100_6_water_supply
062D | 10 81 0A 00 9E 00 00 00; | save $var=pt100_6_water_supply
062E | 10 80 01 01 62 00 00 00; | load shift $hex=62
062F | 22 FF 00 FF 10 00 00 00; | send.modbus $dev=server $reg=255 $len=16
0630 | 01 01 00 00 E0 93 04 00; | wait $sec=30
0631 | 26 12 00 05 02 00 00 00; | read.modbus $dev=18 $reg=5
0632 | 08 0A 36 06 9F 00 00 00; | if equal goto #+4 $var=pt100_6_air_return
0633 | 10 81 0A 00 9F 00 00 00; | save $var=pt100_6_air_return
0634 | 10 80 01 01 63 00 00 00; | load shift $hex=63
0635 | 22 FF 00 FF 10 00 00 00; | send.modbus $dev=server $reg=255 $len=16
0636 | 01 01 00 00 E0 93 04 00; | wait $sec=30
0637 | 26 12 00 06 02 00 00 00; | read.modbus $dev=18 $reg=6
0638 | 08 0A 3C 06 A0 00 00 00; | if equal goto #+4 $var=pt100_6_air_supply
0639 | 10 81 0A 00 A0 00 00 00; | save $var=pt100_6_air_supply
063A | 10 80 01 01 64 00 00 00; | load shift $hex=64
063B | 22 FF 00 FF 10 00 00 00; | send.modbus $dev=server $reg=255 $len=16
063C | 01 01 AD 05 40 77 1B 00; | goto #temp_probe_cycle $min=3

## Settings1
00 | 02; | 2 | MAC Address | 1 |  |  |  |  | Dir: | C:\tini\ModularHotel\ABSlink\RCUmanager\bin\Release
01 | 01; | 1 |  | 2 |  |  |  |  | Settings page: | 0x0007D000
02 | 36; | 54 |  | 3 |  | 19
03 | 7D; | 125 |  | 4 |  | 109
04 | 6D; | 109 |  | 5 |  | 125
05 | 14; | 19 |  | 6 |  | 54
06 | C0; | 192 | Device IP | 1
07 | A8; | 168 |  | 2
08 | 01; | 1 |  | 3
09 | E0; | 224 |  | 4
0A | FF; | 255 | Mask | 1
0B | FF; | 255 |  | 2
0C | FF; | 255 |  | 3
0D | 00; | 0 |  | 4
0E | 82; | 130 | Gateway | 1
0F | 0A; | 10 |  | 2
10 | 01; | 1 |  | 3
11 | 01; | 1 |  | 4
12 | 10; | 16 | Port | Hi | 4096
13 | 00; | 0 |  | Low
14 | 00; | 0 | Devices/EventMap | 1 |  | Device list followed by event map
15 | C0; | 192 |  | 2 |  | (align 4 byte var/dest)
16 | 07; | 7 |  | 3
17 | 00; | 0 |  | 4
18 | 00; | 0 | AutoStart/Program | 1 |  | Autostart followed by program
19 | 80; | 128 | 0=above 63 blocks 80=standard below 63 blocks | 2 |  | (align 4 byte var/dest)
1A | 07; | 7 |  | 3
1B | 00; | 0 |  | 4
1C | 15; | 21 | DeviceNum | 4 |  | Devices number
1D | 04; | 4 | AutostartNum | Space |  | Number of elements in autoexec
1E | 82; | 130 | TH Server | 1 |  | ModBus pseudoadd FF
1F | 0A; | 10 |  | 2
20 | 01; | 1 |  | 3
21 | DC; | 220 |  | 4
22 | E8; | 232 | Site code | 1
23 | 03; | 3 |  | 2
24 | 00; | 0 |  | 3
25 | 00; | 0 |  | 4
26 | 00; | 0 |  | 5
27 | 00; | 0 |  | 6
28 | 00; | 0 |  | 7
29 | 00; | 0 |  | 8
2A | 81; | 129 | Room number | 1
2B | 00; | 0 |  | 2
2C | 00; | 0 | Building/Extension | 1
2D | 00; | 0 |  | 2
2E | 10; | 16 | TH server port | 1
2F | 00; | 0 |  | 2
30 | 53; | 83 | COM1 | Type |  | Master 115k | Processes sheet
31 | 53; | 83 | COM2 | Type |  | Master 115k
32 | 53; | 83 | COM3 | Type |  | Master 9.6k
33 | 00; | 0 | RF | Type |  | Slave 9600
34 | 01; | 1 | TCP/IP | Type |  | Slave
35 | 14; | 20 | COMTimeout | Par secs |  | Max timeout on answer (in 128 1/10000 secs, 20 =1/4 secs)
36 | 20; | 32 | COM Delay 1 | Tick |  | Delay between packets
37 | 32; | 50 | COM Delay 1 | Tick |  | Delay between packets
38 | 20; | 32 | COM Delay 1 | Tick |  | Delay between packets
39 | 07; | 7 | RCU Relay mask |  |  | security block, filter out thermo relays
3A | 05; | 5 | Thermo1 | Device Num |  | TAG
3B | 01; | 1 | Thermo1 | Type |  | 0=Null, 1=TAG base rel 1/0, 2=Tag IOEXP 2nd Bus |  |  | Type Bit 0x80 Copy to TAG 0x40: PT100/Sensor registry in # (3,4,5,6)
3C | 00; | 0 | Thermo1 | Control device |  | 0=RCU, 0000####=control device num - ####0000=sensor device num (devices supported 1-15)
3D | 00; | 0 | Thermo1 | Hot relay |  | 0=Null, 1-31 = rel, 32-39 = 0-10V, 1#OO OCCC Floating valve: # 1relay 8-16 OpenClose |  |  |  |  | Relay are zero based on floating
3E | 20; | 32 | Thermo1 | Cold relay |  | 0=Null, 1-31 = rel, 32-39 = 0-10V, 1#OO OCCC Floating valve: # 1relay 8-16 OpenClose |  |  |  |  | Relay are zero based on floating
3F | 04; | 4 | Thermo1 | Speed1 relay |  | 0=Null, 1-31 = rel, 0x80 no winter, 0x40 no summer, 0x20 0-10V:[ 0x18 0,1,2,3 Analog out, 0x7 % of opening in 8 step: 0, 14, 28, 42, 56, 70, 84, 98]
40 | 03; | 3 | Thermo1 | Speed2 relay |  | 0=Null, 1-31 = rel, 0x80 no winter, 0x40 no summer, 0x20 0-10V:[ 0x18 0,1,2,3 Analog out, 0x7 % of opening in 8 step: 0, 14, 28, 42, 56, 70, 84, 98]
41 | 02; | 2 | Thermo1 | Speed3 relay |  | 0=Null, 1-31 = rel, 0x80 no winter, 0x40 no summer, 0x20 0-10V:[ 0x18 0,1,2,3 Analog out, 0x7 % of opening in 8 step: 0, 14, 28, 42, 56, 70, 84, 98]
42 | 00; | 0 | Thermo1 | Window contact |  | 87th bits 00Rcu/01Tag/10Dev, 20h=1NO 0NC, 00hNone, 0fh #Input
43 | 06; | 6 | Thermo2 | Device Num |  | TAG
44 | 01; | 1 | Thermo2 | Type |  | 0=Null, 1=TAG base rel 1/0
45 | 00; | 0 | Thermo2 | Control device |  | 0=RCU, #=device num
46 | 00; | 0 | Thermo2 | Hot relay |  | 0=Null, 1-31 = rel, 32-33 = 0-10V
47 | 21; | 33 | Thermo2 | Cold relay |  | 0=Null, 1-31 = rel, 32-33 = 0-10V
48 | 06; | 6 | Thermo2 | Speed1 relay |  | 0=Null, 1-31 = rel
49 | 07; | 7 | Thermo2 | Speed2 relay |  | 0=Null, 1-31 = rel
4A | 08; | 8 | Thermo2 | Speed3 relay |  | 0=Null, 1-31 = rel
4B | 00; | 0 | Thermo2 | Window contact |  | 87th bits 00Rcu/01Tag/10Dev, 00hNone, #Input number
4C | 07; | 7 | Thermo3 | Device Num |  | TAG
4D | 01; | 1 | Thermo3 | Type |  | 0=Null, 1=TAG base rel 1/0
4E | 0B; | 11 | Thermo3 | Control device |  | 0=RCU, #=device num
4F | 00; | 0 | Thermo3 | Hot relay |  | 0=Null, 1-31 = rel, 32-33 = 0-10V
50 | 20; | 32 | Thermo3 | Cold relay |  | 0=Null, 1-31 = rel, 32-33 = 0-10V
51 | 03; | 3 | Thermo3 | Speed1 relay |  | 0=Null, 1-31 = rel
52 | 02; | 2 | Thermo3 | Speed2 relay |  | 0=Null, 1-31 = rel
53 | 01; | 1 | Thermo3 | Speed3 relay |  | 0=Null, 1-31 = rel
54 | 00; | 0 | Thermo3 | Window contact |  | 87th bits 00Rcu/01Tag/10Dev, 00hNone, #Input number
55 | 08; | 8 | Thermo4 | Device Num |  | TAG
56 | 01; | 1 | Thermo4 | Type |  | 0=Null, 1=TAG base rel 1/0
57 | 0B; | 11 | Thermo4 | Control device |  | 0=RCU, #=device num
58 | 00; | 0 | Thermo4 | Hot relay |  | 0=Null, 1-31 = rel, 32-33 = 0-10V
59 | 21; | 33 | Thermo4 | Cold relay |  | 0=Null, 1-31 = rel, 32-33 = 0-10V
5A | 04; | 4 | Thermo4 | Speed1 relay |  | 0=Null, 1-31 = rel
5B | 05; | 5 | Thermo4 | Speed2 relay |  | 0=Null, 1-31 = rel
5C | 06; | 6 | Thermo4 | Speed3 relay |  | 0=Null, 1-31 = rel
5D | 00; | 0 | Thermo4 | Window contact |  | 87th bits 00Rcu/01Tag/10Dev, 00hNone, #Input number
5E | 09; | 9 | Thermo5 | Device Num |  | TAG
5F | 01; | 1 | Thermo5 | Type |  | 0=Null, 1=TAG base rel 1/0
60 | 0C; | 12 | Thermo5 | Control device |  | 0=RCU, #=device num
61 | 00; | 0 | Thermo5 | Hot relay |  | 0=Null, 1-31 = rel, 32-33 = 0-10V
62 | 21; | 33 | Thermo5 | Cold relay |  | 0=Null, 1-31 = rel, 32-33 = 0-10V
63 | 01; | 1 | Thermo5 | Speed1 relay |  | 0=Null, 1-31 = rel
64 | 02; | 2 | Thermo5 | Speed2 relay |  | 0=Null, 1-31 = rel
65 | 03; | 3 | Thermo5 | Speed3 relay |  | 0=Null, 1-31 = rel
66 | 00; | 0 | Thermo5 | Window contact |  | 87th bits 00Rcu/01Tag/10Dev, 00hNone, #Input number
67 | 0A; | 10 | Thermo6 | Device Num |  | TAG
68 | 01; | 1 | Thermo6 | Type |  | 0=Null, 1=TAG base rel 1/0
69 | 0C; | 12 | Thermo6 | Control device |  | 0=RCU, #=device num
6A | 00; | 0 | Thermo6 | Hot relay |  | 0=Null, 1-31 = rel, 32-33 = 0-10V
6B | 20; | 32 | Thermo6 | Cold relay |  | 0=Null, 1-31 = rel, 32-33 = 0-10V
6C | 04; | 4 | Thermo6 | Speed1 relay |  | 0=Null, 1-31 = rel
6D | 05; | 5 | Thermo6 | Speed2 relay |  | 0=Null, 1-31 = rel
6E | 06; | 6 | Thermo6 | Speed3 relay |  | 0=Null, 1-31 = rel
6F | 00; | 0 | Thermo6 | Window contact |  | 8th bit 0Rcu/1Tag, 0None, #Input number
70 | 14; | 20 | Thermo* | Speed Ratio |  | FanSpeed=Temperature delta in decimals / ratio
71 | 01; | 1 | Thermo* | Valve Ratio |  | Valve 0-100%= delta temp in cent / ratio
72 | 00; | 0
73 | 00; | 0
74 | 00; | 0 | Thermo* | RunTime Cold | 1 | Running time for the valve in TICK
75 | 00; | 0 | Thermo* | RunTime Cold | 2 | es. 190 sec= 10000*190
76 | 00; | 0 | Thermo* | RunTime Cold | 3 |  | 0 | 00000000
77 | 00; | 0 | Thermo* | RunTime Cold | 4
78 | 00; | 0 | Thermo* | RunTime Hot | 1
79 | 00; | 0 | Thermo* | RunTime Hot | 2
7A | 00; | 0 | Thermo* | RunTime Hot | 3 |  | 0 | 00000000
7B | 00; | 0 | Thermo* | RunTime Hot | 4
7C | 00; | 0
7D | 00; | 0
7E | 00; | 0
7F | 01; | 1
80 | 10; | 16 | Roles opening door | low |  | Permit to define staff open the door
81 | 00; | 0 | Roles opening door | high
82 | 01; | 1 | Ablitate groups opening |  |  | bit1=true
83 | 18; | 24 | Roles blocked by | low |  | HK and HKS
84 | 00; | 0 | flag on event | high
85 | 00; | 0 | RfId mode |  |  | 0=standard, 1=Vingcard mixed
86 | 00; | 0 | RfId data |  |  | On Vingcard mode = starting info for staff
87 | 00; | 0
88 | 01; | 1 | Type of calculation for open valve |  |  | 0=standard, 1=japanese algorithm
89 | 00; | 0
8A | 01; | 1 | Battery if=1 from program, if=0 charging |  |  | bit 0=0 Output on, 1=0 if battery dor lock 100% to-do add new HW
8B | 00; | 0 | Delay on server error |  |  | amount of delay before next send, 0=1 second else (1/10000)<<val
8C | 00; | 0 | FAN remap on valve mode |  |  | 1= fan based on valves according the remap table below
8D | 00; | 0 | Fan1 Fan1 from valve %
8E | 00; | 0 | Fan2 Fan2 from valve %
8F | 00; | 0 | Fan3 Fan3 from valve %
90 | 03; | 3 | BSP1
91 | 00; | 0
92 | 01; | 1
93 | 80; | 128
94 | 00; | 0 | BSP2
95 | 00; | 0
96 | 00; | 0
97 | 00; | 0
98 | 00; | 0 | BSP3
99 | 00; | 0
9A | 00; | 0
9B | 00; | 0
9C | 00; | 0 | BSP4
9D | 00; | 0
9E | 00; | 0
9F | 00; | 0
A0 | 00; | 0 | BSP5
A1 | 00; | 0
A2 | 00; | 0
A3 | 00; | 0
A4 | 00; | 0 | BSP6
A5 | 00; | 0
A6 | 00; | 0
A7 | 00; | 0
A8 | 00; | 0
A9 | 00; | 0
AA | 00; | 0
AB | 00; | 0
AC | 00; | 0
AD | 00; | 0
AE | 00; | 0
AF | 00; | 0
B0 | 00; | 0
B1 | 00; | 0
B2 | 00; | 0
B3 | 00; | 0
B4 | 00; | 0
B5 | 00; | 0
B6 | 00; | 0
B7 | 00; | 0
B8 | 00; | 0
B9 | 00; | 0
BA | 00; | 0
BB | 00; | 0
BC | 00; | 0
BD | 00; | 0
BE | 00; | 0
BF | 00; | 0
C0 | 50; |  | COM4 BusExt |  | !=0 = Activate |  | 3D-5D Kaba - 50 WiFi -10.50.53 ZigBee master 50 vingcard;
C1 | 05; | 1 | COM Ext Type |  | 0, 1=Kaba, 2=WiFi/ZigBee transparent, 3=ZigBeeMaster, 4=WiFiMaster Digi API
C2 | 01; | 1 | Expansio bus type |  | 1=8 relays 2=16inputs
C3 | 00; | 0 | Number of locks |  | Address specified on ZigBee addresses from 0x300
C4 | 00; | 0 | ZeroCrossing on Input 8 | 1 | Delay RelayOn/Off on zero crossing (1 activate, >1 delay in TICK)
C5 | 00; | 0 | ZeroCrossing on Input | 2
C6 | 00; | 0 | ZeroCrossing on Input | 3
C7 | 00; | 0 | ZeroCrossing on Input | 4
C8 | 00; | 0 | Offset GMT time -> UTC | 1 | Offset signed INT 32 bit
C9 | 00; | 0 | params set to AUS time | 2 |  | 0 | GMT
CA | 00; | 0 |  | 3 |  | 0 | val
CB | 00; | 0 |  | 4 |  |  | FFFFFFFF-hex(GMT *3600)
CC | 00; | 0
CD | 00; | 0
CE | 00; | 0
CF | 00; | 0
D0 | 00; | 0
D1 | 00; | 0
D2 | 00; | 0
D3 | 00; | 0
D4 | 00; | 0
D5 | 00; | 0
D6 | 00; | 0
D7 | 00; | 0
D8 | 00; | 0
D9 | 00; | 0
DA | 00; | 0
DB | 00; | 0
DC | 00; | 0
DD | 00; | 0
DE | 00; | 0
DF | 00; | 0
E0 | 00; | 0
E1 | 00; | 0
E2 | 00; | 0
E3 | 00; | 0
E4 | 00; | 0
E5 | 00; | 0
E6 | 00; | 0
E7 | 00; | 0
E8 | 00; | 0
E9 | 00; | 0
EA | 00; | 0
EB | 00; | 0
EC | 00; | 0
ED | 00; | 0
EE | 00; | 0
EF | 00; | 0
F0 | 00; | 0
F1 | 00; | 0
F2 | 00; | 0
F3 | 00; | 0
F4 | 00; | 0
F5 | 00; | 0
F6 | 00; | 0
F7 | 00; | 0
F8 | 00; | 0
F9 | 00; | 0
FA | 00; | 0
FB | 00; | 0
FC | 00; | 0
FD | 00; | 0
FE | 00; | 0
FF | 00; | 0
100 | 02; | 2 | Enabled groups |  | 0 |  | Group | 000-007
101 | 00; | 0 |  |  | 1 |  |  | 008-015
102 | 00; | 0 |  |  | 2 |  |  | 016-023
103 | 00; | 0 |  |  | 3
104 | 00; | 0 |  |  | 4
105 | 00; | 0 |  |  | 5
106 | 00; | 0 |  |  | 6
107 | 00; | 0 |  |  | 7
108 | 00; | 0 |  |  | 8
109 | 00; | 0 |  |  | 9
10A | 00; | 0 |  |  | 10
10B | 00; | 0 |  |  | 11
10C | 00; | 0 |  |  | 12
10D | 00; | 0 |  |  | 13
10E | 00; | 0 |  |  | 14
10F | 00; | 0 |  |  | 15
110 | 00; | 0 |  |  | 16
111 | 00; | 0 |  |  | 17
112 | 00; | 0 |  |  | 18
113 | 00; | 0 |  |  | 19
114 | 00; | 0 |  |  | 20
115 | 00; | 0 |  |  | 21
116 | 00; | 0 |  |  | 22
117 | 00; | 0 |  |  | 23
118 | 00; | 0 |  |  | 24
119 | 00; | 0 |  |  | 25
11A | 00; | 0 |  |  | 26
11B | 00; | 0 |  |  | 27
11C | 00; | 0 |  |  | 28
11D | 00; | 0 |  |  | 29
11E | 00; | 0 |  |  | 30
11F | 00; | 0 |  |  | 31 |  |  | 248-255
120 | 00; | 0
121 | 00; | 0
122 | 00; | 0
123 | 00; | 0
124 | 00; | 0
125 | 00; | 0
126 | 00; | 0
127 | 00; | 0
128 | 00; | 0
129 | 00; | 0
12A | 00; | 0
12B | 00; | 0
12C | 00; | 0
12D | 00; | 0
12E | 00; | 0
12F | 00; | 0
130 | 00; | 0
131 | 00; | 0
132 | 00; | 0
133 | 00; | 0
134 | 00; | 0
135 | 00; | 0
136 | 00; | 0
137 | 00; | 0
138 | 00; | 0
139 | 00; | 0
13A | 00; | 0
13B | 00; | 0
13C | 00; | 0
13D | 00; | 0
13E | 00; | 0 |  |  | 30
13F | 00; | 0 |  |  | 31 |  |  | 248-255
140 | 02; | 2 | Enabled groups IDPG2 |  | 0 |  | Group | 000-007
141 | 00; | 0 |  |  | 1 |  |  | 008-015
142 | 00; | 0 |  |  | 2 |  |  | 016-023
143 | 00; | 0 |  |  | 3
144 | 00; | 0 |  |  | 4
145 | 00; | 0 |  |  | 5
146 | 00; | 0 |  |  | 6
147 | 00; | 0 |  |  | 7
148 | 00; | 0 |  |  | 8
149 | 00; | 0 |  |  | 9
14A | 00; | 0 |  |  | 10
14B | 00; | 0 |  |  | 11
14C | 00; | 0 |  |  | 12
14D | 00; | 0 |  |  | 13
14E | 00; | 0 |  |  | 14
14F | 00; | 0 |  |  | 15
150 | 00; | 0 |  |  | 16
151 | 00; | 0 |  |  | 17
152 | 00; | 0 |  |  | 18
153 | 00; | 0 |  |  | 19
154 | 00; | 0 |  |  | 20
155 | 00; | 0 |  |  | 21
156 | 00; | 0 |  |  | 22
157 | 00; | 0 |  |  | 23
158 | 00; | 0 |  |  | 24
159 | 00; | 0 |  |  | 25
15A | 00; | 0 |  |  | 26
15B | 00; | 0 |  |  | 27
15C | 00; | 0 |  |  | 28
15D | 00; | 0 |  |  | 29
15E | 00; | 0 |  |  | 30
15F | 00; | 0 |  |  | 31 |  |  | 248-255
160 | 02; | 2 | Enabled groups IDPG3 |  | 0 |  | Group | 000-007
161 | 00; | 0 |  |  | 1 |  |  | 008-015
162 | 00; | 0 |  |  | 2 |  |  | 016-023
163 | 00; | 0 |  |  | 3
164 | 00; | 0 |  |  | 4
165 | 00; | 0 |  |  | 5
166 | 00; | 0 |  |  | 6
167 | 00; | 0 |  |  | 7
168 | 00; | 0 |  |  | 8
169 | 00; | 0 |  |  | 9
16A | 00; | 0 |  |  | 10
16B | 00; | 0 |  |  | 11
16C | 00; | 0 |  |  | 12
16D | 00; | 0 |  |  | 13
16E | 00; | 0 |  |  | 14
16F | 00; | 0 |  |  | 15
170 | 00; | 0 |  |  | 16
171 | 00; | 0 |  |  | 17
172 | 00; | 0 |  |  | 18
173 | 00; | 0 |  |  | 19
174 | 00; | 0 |  |  | 20
175 | 00; | 0 |  |  | 21
176 | 00; | 0 |  |  | 22
177 | 00; | 0 |  |  | 23
178 | 00; | 0 |  |  | 24
179 | 00; | 0 |  |  | 25
17A | 00; | 0 |  |  | 26
17B | 00; | 0 |  |  | 27
17C | 00; | 0 |  |  | 28
17D | 00; | 0 |  |  | 29
17E | 00; | 0 |  |  | 30
17F | 00; | 0 |  |  | 31 |  |  | 248-255
180 | 02; | 2 | Enabled groups IDPG4 |  | 0 |  | Group | 000-007
181 | 00; | 0 |  |  | 1 |  |  | 008-015
182 | 00; | 0 |  |  | 2 |  |  | 016-023
183 | 00; | 0 |  |  | 3
184 | 00; | 0 |  |  | 4
185 | 00; | 0 |  |  | 5
186 | 00; | 0 |  |  | 6
187 | 00; | 0 |  |  | 7
188 | 00; | 0 |  |  | 8
189 | 00; | 0 |  |  | 9
18A | 00; | 0 |  |  | 10
18B | 00; | 0 |  |  | 11
18C | 00; | 0 |  |  | 12
18D | 00; | 0 |  |  | 13
18E | 00; | 0 |  |  | 14
18F | 00; | 0 |  |  | 15
190 | 00; | 0 |  |  | 16
191 | 00; | 0 |  |  | 17
192 | 00; | 0 |  |  | 18
193 | 00; | 0 |  |  | 19
194 | 00; | 0 |  |  | 20
195 | 00; | 0 |  |  | 21
196 | 00; | 0 |  |  | 22
197 | 00; | 0 |  |  | 23
198 | 00; | 0 |  |  | 24
199 | 00; | 0 |  |  | 25
19A | 00; | 0 |  |  | 26
19B | 00; | 0 |  |  | 27
19C | 00; | 0 |  |  | 28
19D | 00; | 0 |  |  | 29
19E | 00; | 0 |  |  | 30
19F | 00; | 0 |  |  | 31 |  |  | 248-255
1A0 | 02; | 2 | Enabled groups IDPG5 |  | 0 |  | Group | 000-007
1A1 | 00; | 0 |  |  | 1 |  |  | 008-015
1A2 | 00; | 0 |  |  | 2 |  |  | 016-023
1A3 | 00; | 0 |  |  | 3
1A4 | 00; | 0 |  |  | 4
1A5 | 00; | 0 |  |  | 5
1A6 | 00; | 0 |  |  | 6
1A7 | 00; | 0 |  |  | 7
1A8 | 00; | 0 |  |  | 8
1A9 | 00; | 0 |  |  | 9
1AA | 00; | 0 |  |  | 10
1AB | 00; | 0 |  |  | 11
1AC | 00; | 0 |  |  | 12
1AD | 00; | 0 |  |  | 13
1AE | 00; | 0 |  |  | 14
1AF | 00; | 0 |  |  | 15
1B0 | 00; | 0 |  |  | 16
1B1 | 00; | 0 |  |  | 17
1B2 | 00; | 0 |  |  | 18
1B3 | 00; | 0 |  |  | 19
1B4 | 00; | 0 |  |  | 20
1B5 | 00; | 0 |  |  | 21
1B6 | 00; | 0 |  |  | 22
1B7 | 00; | 0 |  |  | 23
1B8 | 00; | 0 |  |  | 24
1B9 | 00; | 0 |  |  | 25
1BA | 00; | 0 |  |  | 26
1BB | 00; | 0 |  |  | 27
1BC | 00; | 0 |  |  | 28
1BD | 00; | 0 |  |  | 29
1BE | 00; | 0 |  |  | 30
1BF | 00; | 0 |  |  | 31 |  |  | 248-255
1C0 | 02; | 2 | Enabled groups IDPG6 |  | 0 |  | Group | 000-007
1C1 | 00; | 0 |  |  | 1 |  |  | 008-015
1C2 | 00; | 0 |  |  | 2 |  |  | 016-023
1C3 | 00; | 0 |  |  | 3
1C4 | 00; | 0 |  |  | 4
1C5 | 00; | 0 |  |  | 5
1C6 | 00; | 0 |  |  | 6
1C7 | 00; | 0 |  |  | 7
1C8 | 00; | 0 |  |  | 8
1C9 | 00; | 0 |  |  | 9
1CA | 00; | 0 |  |  | 10
1CB | 00; | 0 |  |  | 11
1CC | 00; | 0 |  |  | 12
1CD | 00; | 0 |  |  | 13
1CE | 00; | 0 |  |  | 14
1CF | 00; | 0 |  |  | 15
1D0 | 00; | 0 |  |  | 16
1D1 | 00; | 0 |  |  | 17
1D2 | 00; | 0 |  |  | 18
1D3 | 00; | 0 |  |  | 19
1D4 | 00; | 0 |  |  | 20
1D5 | 00; | 0 |  |  | 21
1D6 | 00; | 0 |  |  | 22
1D7 | 00; | 0 |  |  | 23
1D8 | 00; | 0 |  |  | 24
1D9 | 00; | 0 |  |  | 25
1DA | 00; | 0 |  |  | 26
1DB | 00; | 0 |  |  | 27
1DC | 00; | 0 |  |  | 28
1DD | 00; | 0 |  |  | 29
1DE | 00; | 0 |  |  | 30
1DF | 00; | 0 |  |  | 31 |  |  | 248-255
1E0 | 02; | 2 | Enabled groups IDPG7 |  | 0 |  | Group | 000-007
1E1 | 00; | 0 |  |  | 1 |  |  | 008-015
1E2 | 00; | 0 |  |  | 2 |  |  | 016-023
1E3 | 00; | 0 |  |  | 3
1E4 | 00; | 0 |  |  | 4
1E5 | 00; | 0 |  |  | 5
1E6 | 00; | 0 |  |  | 6
1E7 | 00; | 0 |  |  | 7
1E8 | 00; | 0 |  |  | 8
1E9 | 00; | 0 |  |  | 9
1EA | 00; | 0 |  |  | 10
1EB | 00; | 0 |  |  | 11
1EC | 00; | 0 |  |  | 12
1ED | 00; | 0 |  |  | 13
1EE | 00; | 0 |  |  | 14
1EF | 00; | 0 |  |  | 15
1F0 | 00; | 0 |  |  | 16
1F1 | 00; | 0 |  |  | 17
1F2 | 00; | 0 |  |  | 18
1F3 | 00; | 0 |  |  | 19
1F4 | 00; | 0 |  |  | 20
1F5 | 00; | 0 |  |  | 21
1F6 | 00; | 0 |  |  | 22
1F7 | 00; | 0 |  |  | 23
1F8 | 00; | 0 |  |  | 24
1F9 | 00; | 0 |  |  | 25
1FA | 00; | 0 |  |  | 26
1FB | 00; | 0 |  |  | 27
1FC | 00; | 0 |  |  | 28
1FD | 00; | 0 |  |  | 29
1FE | 00; | 0 |  |  | 30
1FF | 00; | 0 |  |  | 31 |  |  | 248-255
200 | 00; | 0
201 | 00; | 0
202 | 00; | 0
203 | 00; | 0
204 | 00; | 0
205 | 00; | 0
206 | 00; | 0
207 | 00; | 0
208 | 00; | 0
209 | 00; | 0
20A | 00; | 0
20B | 00; | 0
20C | 00; | 0
20D | 00; | 0
20E | 00; | 0
20F | 00; | 0
210 | 00; | 0
211 | 00; | 0
212 | 00; | 0
213 | 00; | 0
214 | 00; | 0
215 | 00; | 0
216 | 00; | 0
217 | 00; | 0
218 | 00; | 0
219 | 00; | 0
21A | 00; | 0
21B | 00; | 0
21C | 00; | 0
21D | 00; | 0
21E | 00; | 0
21F | 00; | 0
220 | 00; | 0
221 | 00; | 0
222 | 00; | 0
223 | 00; | 0
224 | 00; | 0
225 | 00; | 0
226 | 00; | 0
227 | 00; | 0
228 | 00; | 0
229 | 00; | 0
22A | 00; | 0
22B | 00; | 0
22C | 00; | 0
22D | 00; | 0
22E | 00; | 0
22F | 00; | 0
230 | 00; | 0
231 | 00; | 0
232 | 00; | 0
233 | 00; | 0
234 | 00; | 0
235 | 00; | 0
236 | 00; | 0
237 | 00; | 0
238 | 00; | 0
239 | 00; | 0
23A | 00; | 0
23B | 00; | 0
23C | 00; | 0
23D | 00; | 0
23E | 00; | 0
23F | 00; | 0
240 | 00; | 0
241 | 00; | 0
242 | 00; | 0
243 | 00; | 0
244 | 00; | 0
245 | 00; | 0
246 | 00; | 0
247 | 00; | 0
248 | 00; | 0
249 | 00; | 0
24A | 00; | 0
24B | 00; | 0
24C | 00; | 0
24D | 00; | 0
24E | 00; | 0
24F | 00; | 0
250 | 00; | 0
251 | 00; | 0
252 | 00; | 0
253 | 00; | 0
254 | 00; | 0
255 | 00; | 0
256 | 00; | 0
257 | 00; | 0
258 | 00; | 0
259 | 00; | 0
25A | 00; | 0
25B | 00; | 0
25C | 00; | 0
25D | 00; | 0
25E | 00; | 0
25F | 00; | 0
260 | 00; | 0
261 | 00; | 0
262 | 00; | 0
263 | 00; | 0
264 | 00; | 0
265 | 00; | 0
266 | 00; | 0
267 | 00; | 0
268 | 00; | 0
269 | 00; | 0
26A | 00; | 0
26B | 00; | 0
26C | 00; | 0
26D | 00; | 0
26E | 00; | 0
26F | 00; | 0
270 | 00; | 0
271 | 00; | 0
272 | 00; | 0
273 | 00; | 0
274 | 00; | 0
275 | 00; | 0
276 | 00; | 0
277 | 00; | 0
278 | 00; | 0
279 | 00; | 0
27A | 00; | 0
27B | 00; | 0
27C | 00; | 0
27D | 00; | 0
27E | 00; | 0
27F | 00; | 0
280 | 00; | 0
281 | 00; | 0
282 | 00; | 0
283 | 00; | 0
284 | 00; | 0
285 | 00; | 0
286 | 00; | 0
287 | 00; | 0
288 | 00; | 0
289 | 00; | 0
28A | 00; | 0
28B | 00; | 0
28C | 00; | 0
28D | 00; | 0
28E | 00; | 0
28F | 00; | 0
290 | 00; | 0
291 | 00; | 0
292 | 00; | 0
293 | 00; | 0
294 | 00; | 0
295 | 00; | 0
296 | 00; | 0
297 | 00; | 0
298 | 00; | 0
299 | 00; | 0
29A | 00; | 0
29B | 00; | 0
29C | 00; | 0
29D | 00; | 0
29E | 00; | 0
29F | 00; | 0
2A0 | 00; | 0
2A1 | 00; | 0
2A2 | 00; | 0
2A3 | 00; | 0
2A4 | 00; | 0
2A5 | 00; | 0
2A6 | 00; | 0
2A7 | 00; | 0
2A8 | 00; | 0
2A9 | 00; | 0
2AA | 00; | 0
2AB | 00; | 0
2AC | 00; | 0
2AD | 00; | 0
2AE | 00; | 0
2AF | 00; | 0
2B0 | 00; | 0
2B1 | 00; | 0
2B2 | 00; | 0
2B3 | 00; | 0
2B4 | 00; | 0
2B5 | 00; | 0
2B6 | 00; | 0
2B7 | 00; | 0
2B8 | 00; | 0
2B9 | 00; | 0
2BA | 00; | 0
2BB | 00; | 0
2BC | 00; | 0
2BD | 00; | 0
2BE | 00; | 0
2BF | 00; | 0
2C0 | 00; | 0
2C1 | 00; | 0
2C2 | 00; | 0
2C3 | 00; | 0
2C4 | 00; | 0
2C5 | 00; | 0
2C6 | 00; | 0
2C7 | 00; | 0
2C8 | 00; | 0
2C9 | 00; | 0
2CA | 00; | 0
2CB | 00; | 0
2CC | 00; | 0
2CD | 00; | 0
2CE | 00; | 0
2CF | 00; | 0
2D0 | 00; | 0
2D1 | 00; | 0
2D2 | 00; | 0
2D3 | 00; | 0
2D4 | 00; | 0
2D5 | 00; | 0
2D6 | 00; | 0
2D7 | 00; | 0
2D8 | 00; | 0
2D9 | 00; | 0
2DA | 00; | 0
2DB | 00; | 0
2DC | 00; | 0
2DD | 00; | 0
2DE | 00; | 0
2DF | 00; | 0
2E0 | 00; | 0
2E1 | 00; | 0
2E2 | 00; | 0
2E3 | 00; | 0
2E4 | 00; | 0
2E5 | 00; | 0
2E6 | 00; | 0
2E7 | 00; | 0
2E8 | 00; | 0
2E9 | 00; | 0
2EA | 00; | 0
2EB | 00; | 0
2EC | 00; | 0
2ED | 00; | 0
2EE | 00; | 0
2EF | 00; | 0
2F0 | 00; | 0
2F1 | 00; | 0
2F2 | 00; | 0
2F3 | 00; | 0
2F4 | 00; | 0
2F5 | 00; | 0
2F6 | 00; | 0
2F7 | 00; | 0
2F8 | 00; | 0
2F9 | 00; | 0
2FA | 00; | 0
2FB | 00; | 0
2FC | 00; | 0
2FD | 00; | 0
2FE | 00; | 0
2FF | 00; | 0
300 | 00; | 0
301 | 00; | 0
302 | 00; | 0
303 | 00; | 0
304 | 00; | 0
305 | 00; | 0
306 | 00; | 0
307 | 00; | 0
308 | 00; | 0
309 | 00; | 0
30A | 00; | 0
30B | 00; | 0
30C | 00; | 0
30D | 00; | 0
30E | 00; | 0
30F | 00; | 0
310 | 00; | 0
311 | 00; | 0
312 | 00; | 0
313 | 00; | 0
314 | 00; | 0
315 | 00; | 0
316 | 00; | 0
317 | 00; | 0
318 | 00; | 0
319 | 00; | 0
31A | 00; | 0
31B | 00; | 0
31C | 00; | 0
31D | 00; | 0
31E | 00; | 0
31F | 00; | 0
320 | 00; | 0
321 | 00; | 0
322 | 00; | 0
323 | 00; | 0
324 | 00; | 0
325 | 00; | 0
326 | 00; | 0
327 | 00; | 0
328 | 00; | 0
329 | 00; | 0
32A | 00; | 0
32B | 00; | 0
32C | 00; | 0
32D | 00; | 0
32E | 00; | 0
32F | 00; | 0
330 | 00; | 0
331 | 00; | 0
332 | 00; | 0
333 | 00; | 0
334 | 00; | 0
335 | 00; | 0
336 | 00; | 0
337 | 00; | 0
338 | 00; | 0
339 | 00; | 0
33A | 00; | 0
33B | 00; | 0
33C | 00; | 0
33D | 00; | 0
33E | 00; | 0
33F | 00; | 0
340 | 00; | 0
341 | 00; | 0
342 | 00; | 0
343 | 00; | 0
344 | 00; | 0
345 | 00; | 0
346 | 00; | 0
347 | 00; | 0
348 | 00; | 0
349 | 00; | 0
34A | 00; | 0
34B | 00; | 0
34C | 00; | 0
34D | 00; | 0
34E | 00; | 0
34F | 00; | 0
350 | 00; | 0
351 | 00; | 0
352 | 00; | 0
353 | 00; | 0
354 | 00; | 0
355 | 00; | 0
356 | 00; | 0
357 | 00; | 0
358 | 00; | 0
359 | 00; | 0
35A | 00; | 0
35B | 00; | 0
35C | 00; | 0
35D | 00; | 0
35E | 00; | 0
35F | 00; | 0
360 | 00; | 0
361 | 00; | 0
362 | 00; | 0
363 | 00; | 0
364 | 00; | 0
365 | 00; | 0
366 | 00; | 0
367 | 00; | 0
368 | 00; | 0
369 | 00; | 0
36A | 00; | 0
36B | 00; | 0
36C | 00; | 0
36D | 00; | 0
36E | 00; | 0
36F | 00; | 0
370 | 00; | 0
371 | 00; | 0
372 | 00; | 0
373 | 00; | 0
374 | 00; | 0
375 | 00; | 0
376 | 00; | 0
377 | 00; | 0
378 | 00; | 0
379 | 00; | 0
37A | 00; | 0
37B | 00; | 0
37C | 00; | 0
37D | 00; | 0
37E | 00; | 0
37F | 00; | 0
380 | 00; | 0
381 | 00; | 0
382 | 00; | 0
383 | 00; | 0
384 | 00; | 0
385 | 00; | 0
386 | 00; | 0
387 | 00; | 0
388 | 00; | 0
389 | 00; | 0
38A | 00; | 0
38B | 00; | 0
38C | 00; | 0
38D | 00; | 0
38E | 00; | 0
38F | 00; | 0
390 | 00; | 0
391 | 00; | 0
392 | 00; | 0
393 | 00; | 0
394 | 00; | 0
395 | 00; | 0
396 | 00; | 0
397 | 00; | 0
398 | 00; | 0
399 | 00; | 0
39A | 00; | 0
39B | 00; | 0
39C | 00; | 0
39D | 00; | 0
39E | 00; | 0
39F | 00; | 0
3A0 | 00; | 0
3A1 | 00; | 0
3A2 | 00; | 0
3A3 | 00; | 0
3A4 | 00; | 0
3A5 | 00; | 0
3A6 | 00; | 0
3A7 | 00; | 0
3A8 | 00; | 0
3A9 | 00; | 0
3AA | 00; | 0
3AB | 00; | 0
3AC | 00; | 0
3AD | 00; | 0
3AE | 00; | 0
3AF | 00; | 0
3B0 | 00; | 0
3B1 | 00; | 0
3B2 | 00; | 0
3B3 | 00; | 0
3B4 | 00; | 0
3B5 | 00; | 0
3B6 | 00; | 0
3B7 | 00; | 0
3B8 | 00; | 0
3B9 | 00; | 0
3BA | 00; | 0
3BB | 00; | 0
3BC | 00; | 0
3BD | 00; | 0
3BE | 00; | 0
3BF | 00; | 0
3C0 | 00; | 0
3C1 | 00; | 0
3C2 | 00; | 0
3C3 | 00; | 0
3C4 | 00; | 0
3C5 | 00; | 0
3C6 | 00; | 0
3C7 | 00; | 0
3C8 | 00; | 0
3C9 | 00; | 0
3CA | 00; | 0
3CB | 00; | 0
3CC | 00; | 0
3CD | 00; | 0
3CE | 00; | 0
3CF | 00; | 0
3D0 | 00; | 0
3D1 | 00; | 0
3D2 | 00; | 0
3D3 | 00; | 0
3D4 | 00; | 0
3D5 | 00; | 0
3D6 | 00; | 0
3D7 | 00; | 0
3D8 | 00; | 0
3D9 | 00; | 0
3DA | 00; | 0
3DB | 00; | 0
3DC | 00; | 0
3DD | 00; | 0
3DE | 00; | 0
3DF | 00; | 0
3E0 | 00; | 0
3E1 | 00; | 0
3E2 | 00; | 0
3E3 | 00; | 0
3E4 | 00; | 0
3E5 | 00; | 0
3E6 | 00; | 0
3E7 | 00; | 0
3E8 | 00; | 0
3E9 | 00; | 0
3EA | 00; | 0
3EB | 00; | 0
3EC | 00; | 0
3ED | 00; | 0
3EE | 00; | 0
3EF | 00; | 0
3F0 | 00; | 0
3F1 | 00; | 0
3F2 | 00; | 0
3F3 | 00; | 0
3F4 | 00; | 0
3F5 | 00; | 0
3F6 | 00; | 0
3F7 | 00; | 0
3F8 | 00; | 0
3F9 | 00; | 0
3FA | 00; | 0
3FB | 00; | 0
3FC | 00; | 0
3FD | 00; | 0
3FE | 00; | 0
3FF | 00; | 0
400 | 00; | 0
401 | 00; | 0
402 | 00; | 0
403 | 00; | 0
404 | 00; | 0
405 | 00; | 0
406 | 00; | 0
407 | 00; | 0
408 | 00; | 0
409 | 00; | 0
40A | 00; | 0
40B | 00; | 0
40C | 00; | 0
40D | 00; | 0
40E | 00; | 0
40F | 00; | 0
410 | 00; | 0
411 | 00; | 0
412 | 00; | 0
413 | 00; | 0
414 | 00; | 0
415 | 00; | 0
416 | 00; | 0
417 | 00; | 0
418 | 00; | 0
419 | 00; | 0
41A | 00; | 0
41B | 00; | 0
41C | 00; | 0
41D | 00; | 0
41E | 00; | 0
41F | 00; | 0
420 | 00; | 0

## CustomVar1
Variable short name | Description for variable
80 | last_action
81 | temp_user
82 | pir
83 | lockaction | 0=no action in past 60 sec 1=card ok happened in previous 60 sec
84 | rcu2_relays
85 | rcu3_relays
86 | rcu4_relays
87 | backup_thermo1
88 | backup_thermo6
89 | PT100_1_water_return
8A | PT100_1_water_supply
8B | PT100_1_air_return
8C | PT100_1_air_supply
8D | PT100_2_water_return
8E | PT100_2_water_supply
8F | PT100_2_air_return
90 | PT100_2_air_supply
91 | PT100_3_water_return
92 | PT100_3_water_supply
93 | PT100_3_air_return
94 | PT100_3_air_supply
95 | PT100_4_water_return
96 | PT100_4_water_supply
97 | PT100_4_air_return
98 | PT100_4_air_supply
99 | PT100_5_water_return
9A | PT100_5_water_supply
9B | PT100_5_air_return
9C | PT100_5_air_supply
9D | PT100_6_water_return
9E | PT100_6_water_supply
9F | PT100_6_air_return
A0 | PT100_6_air_supply
A1 | PT100_7_water_return
A2 | PT100_7_water_supply
A3 | PT100_7_air_return
A4 | PT100_7_air_supply

## Device2
| ;Devices.hex | [9 empty] | Event map |  |  | Dir: | C:\tini\ModularHotel\ABSlink\RCUmanager\bin\Release
| ;Enum | Type | Id | COM | Pt Event map |  |  |  | lo hi |  | 16bit pt to program |  |  | 0000=none |  |  |  | Enum/Priority
| ;/Priority |  |  |  | lo hi |  | EnumHex | Enum | Progran |  | Start with RCU event |  |  | 8000=activate standard management |  |  |  | Enum is used in multi devices to manage variable offseting
1 | 01 | 06 | 28 | 02 | 21 00 | ;GSW04 A (Bed1) | 00 | 0 | 00 00; | RCU | Startup |  |  | 4000=only on guest presence
2 | 11 | 06 | 29 | 02 | 3C 00 | ;GSW04 B (Bed1) | 01 | 1 | 00 00; |  | Watchdog |  |  | bit 15 permit to flag both (standard+program)
3 | 21 | 06 | 2A | 02 | 57 00 | ;GSW04 C (Bed2) | 02 | 2 | 00 00; |  | Battery | start |  | bit 14 only guest action
4 | 31 | 06 | 2B | 02 | 72 00 | ;GSW04 D (Bed2) | 03 | 3 | 00 00; |  | Battery | end
5 | 41 | 06 | 2C | 02 | 8D 00 | ;GSW04 E (Bed3) | 04 | 4 | 00 00; |  | Battery | low |  | Types
6 | 51 | 06 | 2D | 02 | A8 00 | ;GSW04 F (Bed3) | 05 | 5 | 00 00; |  | Input | 1 on |  | 1 | IDPG
7 | 61 | 06 | 29 | 01 | C3 00 | ;GSW03 A (Bed2 Bathroom) | 06 | 6 | 00 00; |  | Input | 1 off |  | 2 | TIG
8 | 71 | 06 | 2A | 01 | DE 00 | ;GSW03 B (Bed3 Bathroom) | 07 | 7 | 00 00; |  | Input | 2 on |  | 3 | TAG
9 | 81 | 06 | 2B | 01 | F9 00 | ;GSW03 C (Master Bathroom) | 08 | 8 | 00 00; |  | Input | 2 off |  | 4 | IOEXP
10 | 91 | 06 | 2C | 01 | 14 01 | ;GSW02 A (Bed2 Entry) | 09 | 9 | 00 00; |  | Input | 3 on |  | 5 | IODEXP
11 | A1 | 06 | 2D | 01 | 2F 01 | ;GSW02 B (Bed3 Entry) | 0A | 10 | 00 00; |  | Input | 3 off |  | 6 | GSW |  | IOEXP with polling on Input
12 | B1 | 06 | 2E | 01 | 4A 01 | ;GSW02 C (Master Entry) | 0B | 11 | 00 00; |  | Input | 4 on |  | 7 | IOEXPIN
13 | 00 | 00 | 00 | 00 | 00 00 | ; | 0C | 12 | 00 00; |  | Input | 4 off |  | 8 | BSP RF
14 | 00 | 00 | 00 | 00 | 00 00 | ; | 0D | 13 | 00 00; |  | Input | 5 on |  | 9 | BSP wired
15 | 00 | 00 | 00 | 00 | 00 00 | ; | 0E | 14 | 00 00; |  | Input | 5 off |  | 128 | General Modbus
16 | A1 | 06 | 28 | 01 | 65 01 | ;GSW01 (Corridor) | 0F | 15 | 00 00; |  | Input | 6 on |  | 129 | General IP |  | Id+Com=Port Pt=last 2 IP addr
17 | 00 | 00 | 00 | 00 | 00 00 | ; | 10 | 16 | 00 00; |  | Input | 6 off
18 | 00 | 00 | 00 | 00 | 00 00 | ; | 11 | 17 | 00 00; |  | Input | 7 on |  | Id | FF | Server
19 | 00 | 00 | 00 | 00 | 00 00 | ; | 12 | 18 | 00 00; |  | Input | 7 off |  |  | FE | Calling device
20 | 00 | 00 | 00 | 00 | 00 00 | ; | 13 | 19 | 00 00; |  | Input | 8 on
[7 empty] | 14 | 20 | 00 00; |  | Input | 8 off
[7 empty] | 15 | 21 | 00 00; |  | Thermo | on
[7 empty] | 16 | 22 | F3 01; |  | Evt grp write (reg) |  | modbus_manager
[7 empty] | 17 | 23 | 00 00; |  | Evt grp write (reg)
[7 empty] | 18 | 24 | 00 00; |  | MUR | off
[7 empty] | 19 | 25 | 00 00; |  | SOS | on
[7 empty] | 1A | 26 | 00 00; |  | SOS | off
[7 empty] | 1B | 27 | 00 00; |  | Laundry | on
[7 empty] | 1C | 28 | 00 00; |  | Laundry | off
[7 empty] | 1D | 29 | 00 00; |  | Call | on
[7 empty] | 1E | 30 | 00 00; |  | Call | off
[7 empty] | 1F | 31 | 00 00; |  | Card Ok
[7 empty] | 20 | 32 | 00 00; |  | Card Nok
[7 empty] | 21 | 33 | 00 00; | GSW04 A | OffLine
[7 empty] | 22 | 34 | 00 00; |  | Button | 1 on
[7 empty] | 23 | 35 | 00 00; |  | Button | 1 off
[7 empty] | 24 | 36 | 00 00; |  | Button | 2 on
[7 empty] | 25 | 37 | 00 00; |  | Button | 2 off
[7 empty] | 26 | 38 | 00 00; |  | Button | 3 on
[7 empty] | 27 | 39 | 00 00; |  | Button | 3 off
[7 empty] | 28 | 40 | 2E 00; |  | Button | 4 on | gsw04a_btn_4_dnd
[7 empty] | 29 | 41 | 00 00; |  | Button | 4 off
[7 empty] | 2A | 42 | 00 00; |  | Button | 5 on
[7 empty] | 2B | 43 | 00 00; |  | Button | 5 off
[7 empty] | 2C | 44 | 43 00; |  | Button | 6 on | gsw04a_btn_6
[7 empty] | 2D | 45 | 00 00; |  | Button | 6 off
[7 empty] | 2E | 46 | 4C 00; |  | Button | 7 on | gsw04a_btn_7
[7 empty] | 2F | 47 | 00 00; |  | Button | 7 off
[7 empty] | 30 | 48 | 00 00; |  | Button | 8 on
[7 empty] | 31 | 49 | 00 00; |  | Button | 8 off
[7 empty] | 32 | 50 | 50 00; |  | Button | 9 on | gsw04a_btn_9
[7 empty] | 33 | 51 | 00 00; |  | Button | 9 off
[7 empty] | 34 | 52 | 00 00; |  | Button | 10 on
[7 empty] | 35 | 53 | 00 00; |  | Button | 10 off
[7 empty] | 36 | 54 | 00 00; |  | Button | 11 on
[7 empty] | 37 | 55 | 00 00; |  | Button | 11 off
[7 empty] | 38 | 56 | 00 00; |  | Button | 12 on
[7 empty] | 39 | 57 | 00 00; |  | Button | 12 off
[7 empty] | 3A | 58 | 00 00; |  | motion | 13 on
[7 empty] | 3B | 59 | 00 00; |  | motion | 13 off
[7 empty] | 3C | 60 | 00 00; | GSW04 B | OffLine
[7 empty] | 3D | 61 | 00 00; |  | Button | 1 on
[7 empty] | 3E | 62 | 00 00; |  | Button | 1 off
[7 empty] | 3F | 63 | 00 00; |  | Button | 2 on
[7 empty] | 40 | 64 | 00 00; |  | Button | 2 off
[7 empty] | 41 | 65 | 00 00; |  | Button | 3 on
[7 empty] | 42 | 66 | 00 00; |  | Button | 3 off
[7 empty] | 43 | 67 | 5D 00; |  | Button | 4 on | gsw04b_btn_4_dnd
[7 empty] | 44 | 68 | 00 00; |  | Button | 4 off
[7 empty] | 45 | 69 | 00 00; |  | Button | 5 on
[7 empty] | 46 | 70 | 00 00; |  | Button | 5 off
[7 empty] | 47 | 71 | 72 00; |  | Button | 6 on | gsw04b_btn_6
[7 empty] | 48 | 72 | 00 00; |  | Button | 6 off
[7 empty] | 49 | 73 | 7B 00; |  | Button | 7 on | gsw04b_btn_7
[7 empty] | 4A | 74 | 00 00; |  | Button | 7 off
[7 empty] | 4B | 75 | 00 00; |  | Button | 8 on
[7 empty] | 4C | 76 | 00 00; |  | Button | 8 off
[7 empty] | 4D | 77 | 7F 00; |  | Button | 9 on | gsw04b_btn_9
[7 empty] | 4E | 78 | 00 00; |  | Button | 9 off
[7 empty] | 4F | 79 | 00 00; |  | Button | 10 on
[7 empty] | 50 | 80 | 00 00; |  | Button | 10 off
[7 empty] | 51 | 81 | 00 00; |  | Button | 11 on
[7 empty] | 52 | 82 | 00 00; |  | Button | 11 off
[7 empty] | 53 | 83 | 00 00; |  | Button | 12 on
[7 empty] | 54 | 84 | 00 00; |  | Button | 12 off
[7 empty] | 55 | 85 | 00 00; |  | motion | 13 on
[7 empty] | 56 | 86 | 00 00; |  | motion | 13 off
[7 empty] | 57 | 87 | 00 00; | GSW04 C | OffLine
[7 empty] | 58 | 88 | 00 00; |  | Button | 1 on
[7 empty] | 59 | 89 | 00 00; |  | Button | 1 off
[7 empty] | 5A | 90 | 00 00; |  | Button | 2 on
[7 empty] | 5B | 91 | 00 00; |  | Button | 2 off
[7 empty] | 5C | 92 | 00 00; |  | Button | 3 on
[7 empty] | 5D | 93 | 00 00; |  | Button | 3 off
[7 empty] | 5E | 94 | 8C 00; |  | Button | 4 on | gsw04c_btn_4_dnd
[7 empty] | 5F | 95 | 00 00; |  | Button | 4 off
[7 empty] | 60 | 96 | 00 00; |  | Button | 5 on
[7 empty] | 61 | 97 | 00 00; |  | Button | 5 off
[7 empty] | 62 | 98 | A1 00; |  | Button | 6 on | gsw04c_btn_6
[7 empty] | 63 | 99 | 00 00; |  | Button | 6 off
[7 empty] | 64 | 100 | AA 00; |  | Button | 7 on | gsw04c_btn_7
[7 empty] | 65 | 101 | 00 00; |  | Button | 7 off
[7 empty] | 66 | 102 | 00 00; |  | Button | 8 on
[7 empty] | 67 | 103 | 00 00; |  | Button | 8 off
[7 empty] | 68 | 104 | AE 00; |  | Button | 9 on | gsw04c_btn_9
[7 empty] | 69 | 105 | 00 00; |  | Button | 9 off
[7 empty] | 6A | 106 | 00 00; |  | Button | 10 on
[7 empty] | 6B | 107 | 00 00; |  | Button | 10 off
[7 empty] | 6C | 108 | 00 00; |  | Button | 11 on
[7 empty] | 6D | 109 | 00 00; |  | Button | 11 off
[7 empty] | 6E | 110 | 00 00; |  | Button | 12 on
[7 empty] | 6F | 111 | 00 00; |  | Button | 12 off
[7 empty] | 70 | 112 | 00 00; |  | motion | 13 on
[7 empty] | 71 | 113 | 00 00; |  | motion | 13 off
[7 empty] | 72 | 114 | 00 00; | GSW04 D | OffLine
[7 empty] | 73 | 115 | 00 00; |  | Button | 1 on
[7 empty] | 74 | 116 | 00 00; |  | Button | 1 off
[7 empty] | 75 | 117 | 00 00; |  | Button | 2 on
[7 empty] | 76 | 118 | 00 00; |  | Button | 2 off
[7 empty] | 77 | 119 | 00 00; |  | Button | 3 on
[7 empty] | 78 | 120 | 00 00; |  | Button | 3 off
[7 empty] | 79 | 121 | BB 00; |  | Button | 4 on | gsw04d_btn_4_dnd
[7 empty] | 7A | 122 | 00 00; |  | Button | 4 off
[7 empty] | 7B | 123 | 00 00; |  | Button | 5 on
[7 empty] | 7C | 124 | 00 00; |  | Button | 5 off
[7 empty] | 7D | 125 | D0 00; |  | Button | 6 on | gsw04d_btn_6
[7 empty] | 7E | 126 | 00 00; |  | Button | 6 off
[7 empty] | 7F | 127 | D9 00; |  | Button | 7 on | gsw04d_btn_7
[7 empty] | 80 | 128 | 00 00; |  | Button | 7 off
[7 empty] | 81 | 129 | 00 00; |  | Button | 8 on
[7 empty] | 82 | 130 | 00 00; |  | Button | 8 off
[7 empty] | 83 | 131 | DD 00; |  | Button | 9 on | gsw04d_btn_9
[7 empty] | 84 | 132 | 00 00; |  | Button | 9 off
[7 empty] | 85 | 133 | 00 00; |  | Button | 10 on
[7 empty] | 86 | 134 | 00 00; |  | Button | 10 off
[7 empty] | 87 | 135 | 00 00; |  | Button | 11 on
[7 empty] | 88 | 136 | 00 00; |  | Button | 11 off
[7 empty] | 89 | 137 | 00 00; |  | Button | 12 on
[7 empty] | 8A | 138 | 00 00; |  | Button | 12 off
[7 empty] | 8B | 139 | 00 00; |  | motion | 13 on
[7 empty] | 8C | 140 | 00 00; |  | motion | 13 off
[7 empty] | 8D | 141 | 00 00; | GSW04 E | OffLine
[7 empty] | 8E | 142 | 00 00; |  | Button | 1 on
[7 empty] | 8F | 143 | 00 00; |  | Button | 1 off
[7 empty] | 90 | 144 | 00 00; |  | Button | 2 on
[7 empty] | 91 | 145 | 00 00; |  | Button | 2 off
[7 empty] | 92 | 146 | 00 00; |  | Button | 3 on
[7 empty] | 93 | 147 | 00 00; |  | Button | 3 off
[7 empty] | 94 | 148 | EA 00; |  | Button | 4 on | gsw04e_btn_4_dnd
[7 empty] | 95 | 149 | 00 00; |  | Button | 4 off
[7 empty] | 96 | 150 | 00 00; |  | Button | 5 on
[7 empty] | 97 | 151 | 00 00; |  | Button | 5 off
[7 empty] | 98 | 152 | FF 00; |  | Button | 6 on | gsw04e_btn_6
[7 empty] | 99 | 153 | 00 00; |  | Button | 6 off
[7 empty] | 9A | 154 | 08 01; |  | Button | 7 on | gsw04e_btn_7
[7 empty] | 9B | 155 | 00 00; |  | Button | 7 off
[7 empty] | 9C | 156 | 00 00; |  | Button | 8 on
[7 empty] | 9D | 157 | 00 00; |  | Button | 8 off
[7 empty] | 9E | 158 | 0C 01; |  | Button | 9 on | gsw04e_btn_9
[7 empty] | 9F | 159 | 00 00; |  | Button | 9 off
[7 empty] | A0 | 160 | 00 00; |  | Button | 10 on
[7 empty] | A1 | 161 | 00 00; |  | Button | 10 off
[7 empty] | A2 | 162 | 00 00; |  | Button | 11 on
[7 empty] | A3 | 163 | 00 00; |  | Button | 11 off
[7 empty] | A4 | 164 | 00 00; |  | Button | 12 on
[7 empty] | A5 | 165 | 00 00; |  | Button | 12 off
[7 empty] | A6 | 166 | 00 00; |  | motion | 13 on
[7 empty] | A7 | 167 | 00 00; |  | motion | 13 off
[7 empty] | A8 | 168 | 00 00; | GSW04 F | OffLine
[7 empty] | A9 | 169 | 00 00; |  | Button | 1 on
[7 empty] | AA | 170 | 00 00; |  | Button | 1 off
[7 empty] | AB | 171 | 00 00; |  | Button | 2 on
[7 empty] | AC | 172 | 00 00; |  | Button | 2 off
[7 empty] | AD | 173 | 00 00; |  | Button | 3 on
[7 empty] | AE | 174 | 00 00; |  | Button | 3 off
[7 empty] | AF | 175 | 19 01; |  | Button | 4 on | gsw04f_btn_4_dnd
[7 empty] | B0 | 176 | 00 00; |  | Button | 4 off
[7 empty] | B1 | 177 | 00 00; |  | Button | 5 on
[7 empty] | B2 | 178 | 00 00; |  | Button | 5 off
[7 empty] | B3 | 179 | 2E 01; |  | Button | 6 on | gsw04f_btn_6
[7 empty] | B4 | 180 | 00 00; |  | Button | 6 off
[7 empty] | B5 | 181 | 37 01; |  | Button | 7 on | gsw04f_btn_7
[7 empty] | B6 | 182 | 00 00; |  | Button | 7 off
[7 empty] | B7 | 183 | 00 00; |  | Button | 8 on
[7 empty] | B8 | 184 | 00 00; |  | Button | 8 off
[7 empty] | B9 | 185 | 3B 01; |  | Button | 9 on | gsw04f_btn_9
[7 empty] | BA | 186 | 00 00; |  | Button | 9 off
[7 empty] | BB | 187 | 00 00; |  | Button | 10 on
[7 empty] | BC | 188 | 00 00; |  | Button | 10 off
[7 empty] | BD | 189 | 00 00; |  | Button | 11 on
[7 empty] | BE | 190 | 00 00; |  | Button | 11 off
[7 empty] | BF | 191 | 00 00; |  | Button | 12 on
[7 empty] | C0 | 192 | 00 00; |  | Button | 12 off
[7 empty] | C1 | 193 | 00 00; |  | motion | 13 on
[7 empty] | C2 | 194 | 00 00; |  | motion | 13 off
[7 empty] | C3 | 195 | 00 00; | GSW03 A | OffLine
[7 empty] | C4 | 196 | 00 00; |  | Button | 1 on
[7 empty] | C5 | 197 | 00 00; |  | Button | 1 off
[7 empty] | C6 | 198 | 00 00; |  | Button | 2 on
[7 empty] | C7 | 199 | 00 00; |  | Button | 2 off
[7 empty] | C8 | 200 | 00 00; |  | Button | 3 on
[7 empty] | C9 | 201 | 00 00; |  | Button | 3 off
[7 empty] | CA | 202 | 42 01; |  | Button | 4 on | gsw03a_btn_4
[7 empty] | CB | 203 | 00 00; |  | Button | 4 off
[7 empty] | CC | 204 | 4A 01; |  | Button | 5 on | gsw03a_btn_5
[7 empty] | CD | 205 | 00 00; |  | Button | 5 off
[7 empty] | CE | 206 | 4D 01; |  | Button | 6 on | gsw03a_btn_6
[7 empty] | CF | 207 | 00 00; |  | Button | 6 off
[7 empty] | D0 | 208 | 00 00; |  | Button | 7 on
[7 empty] | D1 | 209 | 00 00; |  | Button | 7 off
[7 empty] | D2 | 210 | 00 00; |  | Button | 8 on
[7 empty] | D3 | 211 | 00 00; |  | Button | 8 off
[7 empty] | D4 | 212 | 00 00; |  | Button | 9 on
[7 empty] | D5 | 213 | 00 00; |  | Button | 9 off
[7 empty] | D6 | 214 | 00 00; |  | Button | 10 on
[7 empty] | D7 | 215 | 00 00; |  | Button | 10 off
[7 empty] | D8 | 216 | 00 00; |  | Button | 11 on
[7 empty] | D9 | 217 | 00 00; |  | Button | 11 off
[7 empty] | DA | 218 | 00 00; |  | Button | 12 on
[7 empty] | DB | 219 | 00 00; |  | Button | 12 off
[7 empty] | DC | 220 | 00 00; |  | motion | 13 on
[7 empty] | DD | 221 | 00 00; |  | motion | 13 off
[7 empty] | DE | 222 | 00 00; | GSW03 B | OffLine
[7 empty] | DF | 223 | 00 00; |  | Button | 1 on
[7 empty] | E0 | 224 | 00 00; |  | Button | 1 off
[7 empty] | E1 | 225 | 00 00; |  | Button | 2 on
[7 empty] | E2 | 226 | 00 00; |  | Button | 2 off
[7 empty] | E3 | 227 | 00 00; |  | Button | 3 on
[7 empty] | E4 | 228 | 00 00; |  | Button | 3 off
[7 empty] | E5 | 229 | 53 01; |  | Button | 4 on | gsw03b_btn_4
[7 empty] | E6 | 230 | 00 00; |  | Button | 4 off
[7 empty] | E7 | 231 | 5B 01; |  | Button | 5 on | gsw03b_btn_5
[7 empty] | E8 | 232 | 00 00; |  | Button | 5 off
[7 empty] | E9 | 233 | 5E 01; |  | Button | 6 on | gsw03b_btn_6
[7 empty] | EA | 234 | 00 00; |  | Button | 6 off
[7 empty] | EB | 235 | 00 00; |  | Button | 7 on
[7 empty] | EC | 236 | 00 00; |  | Button | 7 off
[7 empty] | ED | 237 | 00 00; |  | Button | 8 on
[7 empty] | EE | 238 | 00 00; |  | Button | 8 off
[7 empty] | EF | 239 | 00 00; |  | Button | 9 on
[7 empty] | F0 | 240 | 00 00; |  | Button | 9 off
[7 empty] | F1 | 241 | 00 00; |  | Button | 10 on
[7 empty] | F2 | 242 | 00 00; |  | Button | 10 off
[7 empty] | F3 | 243 | 00 00; |  | Button | 11 on
[7 empty] | F4 | 244 | 00 00; |  | Button | 11 off
[7 empty] | F5 | 245 | 00 00; |  | Button | 12 on
[7 empty] | F6 | 246 | 00 00; |  | Button | 12 off
[7 empty] | F7 | 247 | 00 00; |  | motion | 13 on
[7 empty] | F8 | 248 | 00 00; |  | motion | 13 off
[7 empty] | F9 | 249 | 00 00; | GSW03 C | OffLine
[7 empty] | FA | 250 | 00 00; |  | Button | 1 on
[7 empty] | FB | 251 | 00 00; |  | Button | 1 off
[7 empty] | FC | 252 | 00 00; |  | Button | 2 on
[7 empty] | FD | 253 | 00 00; |  | Button | 2 off
[7 empty] | FE | 254 | 00 00; |  | Button | 3 on
[7 empty] | FF | 255 | 00 00; |  | Button | 3 off
[7 empty] | 100 | 256 | 64 01; |  | Button | 4 on | gsw03c_btn_4
[7 empty] | 101 | 257 | 00 00; |  | Button | 4 off
[7 empty] | 102 | 258 | 6C 01; |  | Button | 5 on | gsw03c_btn_5
[7 empty] | 103 | 259 | 00 00; |  | Button | 5 off
[7 empty] | 104 | 260 | 6F 01; |  | Button | 6 on | gsw03c_btn_6
[7 empty] | 105 | 261 | 00 00; |  | Button | 6 off
[7 empty] | 106 | 262 | 00 00; |  | Button | 7 on
[7 empty] | 107 | 263 | 00 00; |  | Button | 7 off
[7 empty] | 108 | 264 | 00 00; |  | Button | 8 on
[7 empty] | 109 | 265 | 00 00; |  | Button | 8 off
[7 empty] | 10A | 266 | 00 00; |  | Button | 9 on
[7 empty] | 10B | 267 | 00 00; |  | Button | 9 off
[7 empty] | 10C | 268 | 00 00; |  | Button | 10 on
[7 empty] | 10D | 269 | 00 00; |  | Button | 10 off
[7 empty] | 10E | 270 | 00 00; |  | Button | 11 on
[7 empty] | 10F | 271 | 00 00; |  | Button | 11 off
[7 empty] | 110 | 272 | 00 00; |  | Button | 12 on
[7 empty] | 111 | 273 | 00 00; |  | Button | 12 off
[7 empty] | 112 | 274 | 00 00; |  | motion | 13 on
[7 empty] | 113 | 275 | 00 00; |  | motion | 13 off
[7 empty] | 114 | 276 | 00 00; | GSW02 A | OffLine
[7 empty] | 115 | 277 | 00 00; |  | Button | 1 on
[7 empty] | 116 | 278 | 00 00; |  | Button | 1 off
[7 empty] | 117 | 279 | 00 00; |  | Button | 2 on
[7 empty] | 118 | 280 | 00 00; |  | Button | 2 off
[7 empty] | 119 | 281 | 00 00; |  | Button | 3 on
[7 empty] | 11A | 282 | 00 00; |  | Button | 3 off
[7 empty] | 11B | 283 | 75 01; |  | Button | 4 on | gsw02a_btn_4
[7 empty] | 11C | 284 | 00 00; |  | Button | 4 off
[7 empty] | 11D | 285 | 00 00; |  | Button | 5 on
[7 empty] | 11E | 286 | 00 00; |  | Button | 5 off
[7 empty] | 11F | 287 | 7D 01; |  | Button | 6 on | gsw02a_btn_6
[7 empty] | 120 | 288 | 00 00; |  | Button | 6 off
[7 empty] | 121 | 289 | 00 00; |  | Button | 7 on
[7 empty] | 122 | 290 | 00 00; |  | Button | 7 off
[7 empty] | 123 | 291 | 00 00; |  | Button | 8 on
[7 empty] | 124 | 292 | 00 00; |  | Button | 8 off
[7 empty] | 125 | 293 | 00 00; |  | Button | 9 on
[7 empty] | 126 | 294 | 00 00; |  | Button | 9 off
[7 empty] | 127 | 295 | 00 00; |  | Button | 10 on
[7 empty] | 128 | 296 | 00 00; |  | Button | 10 off
[7 empty] | 129 | 297 | 00 00; |  | Button | 11 on
[7 empty] | 12A | 298 | 00 00; |  | Button | 11 off
[7 empty] | 12B | 299 | 00 00; |  | Button | 12 on
[7 empty] | 12C | 300 | 00 00; |  | Button | 12 off
[7 empty] | 12D | 301 | 00 00; |  | motion | 13 on
[7 empty] | 12E | 302 | 00 00; |  | motion | 13 off
[7 empty] | 12F | 303 | 00 00; | GSW02 B | OffLine
[7 empty] | 130 | 304 | 00 00; |  | Button | 1 on
[7 empty] | 131 | 305 | 00 00; |  | Button | 1 off
[7 empty] | 132 | 306 | 00 00; |  | Button | 2 on
[7 empty] | 133 | 307 | 00 00; |  | Button | 2 off
[7 empty] | 134 | 308 | 00 00; |  | Button | 3 on
[7 empty] | 135 | 309 | 00 00; |  | Button | 3 off
[7 empty] | 136 | 310 | 83 01; |  | Button | 4 on | gsw02b_btn_4
[7 empty] | 137 | 311 | 00 00; |  | Button | 4 off
[7 empty] | 138 | 312 | 00 00; |  | Button | 5 on
[7 empty] | 139 | 313 | 00 00; |  | Button | 5 off
[7 empty] | 13A | 314 | 8B 01; |  | Button | 6 on | gsw02b_btn_6
[7 empty] | 13B | 315 | 00 00; |  | Button | 6 off
[7 empty] | 13C | 316 | 00 00; |  | Button | 7 on
[7 empty] | 13D | 317 | 00 00; |  | Button | 7 off
[7 empty] | 13E | 318 | 00 00; |  | Button | 8 on
[7 empty] | 13F | 319 | 00 00; |  | Button | 8 off
[7 empty] | 140 | 320 | 00 00; |  | Button | 9 on
[7 empty] | 141 | 321 | 00 00; |  | Button | 9 off
[7 empty] | 142 | 322 | 00 00; |  | Button | 10 on
[7 empty] | 143 | 323 | 00 00; |  | Button | 10 off
[7 empty] | 144 | 324 | 00 00; |  | Button | 11 on
[7 empty] | 145 | 325 | 00 00; |  | Button | 11 off
[7 empty] | 146 | 326 | 00 00; |  | Button | 12 on
[7 empty] | 147 | 327 | 00 00; |  | Button | 12 off
[7 empty] | 148 | 328 | 00 00; |  | motion | 13 on
[7 empty] | 149 | 329 | 00 00; |  | motion | 13 off
[7 empty] | 14A | 330 | 00 00; | GSW02 C | OffLine
[7 empty] | 14B | 331 | 00 00; |  | Button | 1 on
[7 empty] | 14C | 332 | 00 00; |  | Button | 1 off
[7 empty] | 14D | 333 | 00 00; |  | Button | 2 on
[7 empty] | 14E | 334 | 00 00; |  | Button | 2 off
[7 empty] | 14F | 335 | 00 00; |  | Button | 3 on
[7 empty] | 150 | 336 | 00 00; |  | Button | 3 off
[7 empty] | 151 | 337 | 91 01; |  | Button | 4 on | gsw02c_btn_4
[7 empty] | 152 | 338 | 00 00; |  | Button | 4 off
[7 empty] | 153 | 339 | 00 00; |  | Button | 5 on
[7 empty] | 154 | 340 | 00 00; |  | Button | 5 off
[7 empty] | 155 | 341 | 99 01; |  | Button | 6 on | gsw02c_btn_6
[7 empty] | 156 | 342 | 00 00; |  | Button | 6 off
[7 empty] | 157 | 343 | 00 00; |  | Button | 7 on
[7 empty] | 158 | 344 | 00 00; |  | Button | 7 off
[7 empty] | 159 | 345 | 00 00; |  | Button | 8 on
[7 empty] | 15A | 346 | 00 00; |  | Button | 8 off
[7 empty] | 15B | 347 | 00 00; |  | Button | 9 on
[7 empty] | 15C | 348 | 00 00; |  | Button | 9 off
[7 empty] | 15D | 349 | 00 00; |  | Button | 10 on
[7 empty] | 15E | 350 | 00 00; |  | Button | 10 off
[7 empty] | 15F | 351 | 00 00; |  | Button | 11 on
[7 empty] | 160 | 352 | 00 00; |  | Button | 11 off
[7 empty] | 161 | 353 | 00 00; |  | Button | 12 on
[7 empty] | 162 | 354 | 00 00; |  | Button | 12 off
[7 empty] | 163 | 355 | 00 00; |  | motion | 13 on
[7 empty] | 164 | 356 | 00 00; |  | motion | 13 off
[7 empty] | 165 | 357 | 00 00; | GSW01 | OffLine
[7 empty] | 166 | 358 | 00 00; |  | Button | 1 on
[7 empty] | 167 | 359 | 00 00; |  | Button | 1 off
[7 empty] | 168 | 360 | 00 00; |  | Button | 2 on
[7 empty] | 169 | 361 | 00 00; |  | Button | 2 off
[7 empty] | 16A | 362 | 00 00; |  | Button | 3 on
[7 empty] | 16B | 363 | 00 00; |  | Button | 3 off
[7 empty] | 16C | 364 | 00 00; |  | Button | 4 on
[7 empty] | 16D | 365 | 00 00; |  | Button | 4 off
[7 empty] | 16E | 366 | 9F 01; |  | Button | 5 on | gsw01_btn_5
[7 empty] | 16F | 367 | 00 00; |  | Button | 5 off
[7 empty] | 170 | 368 | 00 00; |  | Button | 6 on
[7 empty] | 171 | 369 | 00 00; |  | Button | 6 off
[7 empty] | 172 | 370 | 00 00; |  | Button | 7 on
[7 empty] | 173 | 371 | 00 00; |  | Button | 7 off
[7 empty] | 174 | 372 | 00 00; |  | Button | 8 on
[7 empty] | 175 | 373 | 00 00; |  | Button | 8 off
[7 empty] | 176 | 374 | 00 00; |  | Button | 9 on
[7 empty] | 177 | 375 | 00 00; |  | Button | 9 off
[7 empty] | 178 | 376 | 00 00; |  | Button | 10 on
[7 empty] | 179 | 377 | 00 00; |  | Button | 10 off
[7 empty] | 17A | 378 | 00 00; |  | Button | 11 on
[7 empty] | 17B | 379 | 00 00; |  | Button | 11 off
[7 empty] | 17C | 380 | 00 00; |  | Button | 12 on
[7 empty] | 17D | 381 | 00 00; |  | Button | 12 off
[7 empty] | 17E | 382 | 00 00; |  | motion | 13 on
[7 empty] | 17F | 383 | 00 00; |  | motion | 13 off

## XCODE2
XCODE [0.9,2]
0 | #startup
1 | version [35561452341814213551145390817034,9]
2 | goto #debugging
3 | reserved for ipad
4 | reserved for ipad
5 | reserved for ipad
6 | reserved for ipad
7 | reserved for ipad
8 | reserved for ipad
9 | reserved for ipad
10 | reserved for ipad
11 | reserved for ipad
12 | reserved for ipad
13 | reserved for ipad
14 | reserved for ipad
15 | reserved for ipad
16 | reserved for ipad
17 | reserved for ipad
18 | reserved for ipad
19 | reserved for ipad
20 | reserved for ipad
21 | reserved for ipad
22 | reserved for ipad
23 | goto #checkout
24 | goto #checkin
25
26 | function startup
27 | //send.modbus $dev=server $reg=0 $dec=0
28 | send.modbus $type=gsw $reg=15 $dec=80*10
29 | send.modbus $type=gsw $reg=16 $dec=30*10
30 | reuse #refresh_workflow_panels $sec=5
31 | wait $sec=5
32 | m_notify.set $dec=0
33 | exit
34
35
36 | function debugging
37 | debug
38 | exit
39
40
41 | //function gsw_motion_settings
42 | //send.modbus $dev=gsw1 $reg=80 $hex=63
43 | //send.modbus $dev=gsw1 $reg=81 $hex=15E
44 | //send.modbus $dev=gsw1 $reg=82 $hex=02
45 | //exit
46
47
48 | //function thermo_cycle
49 | //send.modbus $dev=server $reg=14 $len=16
50 | //exit
51
52 | //function dev_offline
53 | //send.modbus $dev=server $reg=8 $len=4
54 | //exit
55
56
57
58
59
60
61 | function checkout
62 | exit
63
64
65
66 | function checkin
67 | goto #checkout
68 | exit
69
70
71
72
73
74
75
76
77 | function GSW04A_refresh | ok
78 | load $var=workflow
79 | If equal goto #3 $dec=7
80 | load $hex=11440
81 | goto #2
82 | load $hex=11480
83 | save $var=gs1
84 | math.and $hex=10080 //with night light
85 | send.modbus $dev=01 $reg=13 $len=4
86 | exit
87 | function GSW04A_btn_4_dnd
88 | load $hex=11480
89 | send.modbus $dev=01 $reg=13 $len=4
90 | load $var=workflow
91 | If not equal goto #+5 $dec=7
92 | load $dec=0
93 | save $var=workflow
94 | load $hex=11440
95 | goto #+4
96 | load $dec=7
97 | save $var=workflow
98 | load $hex=11480
99 | send.modbus $dev=01 $reg=13 $len=4
100 | save $var=gs1
101 | reuse #GSW04A_refresh $sec=15
102 | reuse #gsw04b_refresh
103 | reuse #gsw04c_refresh
104 | reuse #gsw04d_refresh
105 | reuse #gsw04e_refresh
106 | reuse #gsw04f_refresh
107 | reuse #dnd_send
108 | exit
109 | function GSW04A_btn_6
110 | reuse #bed1_master
111 | load $var=gs1
112 | math.and $hex=FFF3FF
113 | function GSW04A_btn_common
114 | send.modbus $dev=01 $reg=13 $len=4
115 | wait $sec=0.15
116 | load $var=gs1
117 | send.modbus $dev=01 $reg=13 $len=4
118 | reuse #GSW04A_refresh $sec=15
119 | exit
120 | function GSW04A_btn_7
121 | reuse #bed1_relax
122 | load $var=gs1
123 | math.and $hex=FFCFFF
124 | goto #GSW04A_btn_common
125 | function GSW04A_btn_9
126 | reuse #bed1_night
127 | load $var=gs1
128 | math.and $hex=FCFFFF
129 | goto #GSW04A_btn_common
130
131
132
133 | function GSW04B_refresh | ok
134 | load $var=workflow
135 | If equal goto #3 $dec=7
136 | load $hex=11440
137 | goto #2
138 | load $hex=11480
139 | save $var=gs2
140 | math.and $hex=10080 //with night light
141 | send.modbus $dev=02 $reg=13 $len=4
142 | exit
143 | function GSW04B_btn_4_dnd
144 | load $hex=11480
145 | send.modbus $dev=02 $reg=13 $len=4
146 | load $var=workflow
147 | If not equal goto #+5 $dec=7
148 | load $dec=0
149 | save $var=workflow
150 | load $hex=11440
151 | goto #+4
152 | load $dec=7
153 | save $var=workflow
154 | load $hex=11480
155 | send.modbus $dev=02 $reg=13 $len=4
156 | save $var=gs2
157 | reuse #GSW04B_refresh $sec=15
158 | reuse #gsw04a_refresh
159 | reuse #gsw04c_refresh
160 | reuse #gsw04d_refresh
161 | reuse #gsw04e_refresh
162 | reuse #gsw04f_refresh
163 | reuse #dnd_send
164 | exit
165 | function GSW04B_btn_6
166 | reuse #bed1_master
167 | load $var=gs2
168 | math.and $hex=FFF3FF
169 | function GSW04B_btn_common
170 | send.modbus $dev=02 $reg=13 $len=4
171 | wait $sec=0.15
172 | load $var=gs2
173 | send.modbus $dev=02 $reg=13 $len=4
174 | reuse #GSW04B_refresh $sec=15
175 | exit
176 | function GSW04B_btn_7
177 | reuse #bed1_relax
178 | load $var=gs2
179 | math.and $hex=FFCFFF
180 | goto #GSW04B_btn_common
181 | function GSW04B_btn_9
182 | reuse #bed1_night
183 | load $var=gs2
184 | math.and $hex=FCFFFF
185 | goto #GSW04B_btn_common
186
187
188
189
190
191
192 | function GSW04C_refresh | ok
193 | load $var=workflow
194 | If equal goto #3 $dec=7
195 | load $hex=11440
196 | goto #2
197 | load $hex=11480
198 | save $var=gs3
199 | math.and $hex=10080 //with night light
200 | send.modbus $dev=03 $reg=13 $len=4
201 | exit
202 | function GSW04C_btn_4_dnd
203 | load $hex=11480
204 | send.modbus $dev=03 $reg=13 $len=4
205 | load $var=workflow
206 | If not equal goto #+5 $dec=7
207 | load $dec=0
208 | save $var=workflow
209 | load $hex=11440
210 | goto #4
211 | load $dec=7
212 | save $var=workflow
213 | load $hex=11480
214 | send.modbus $dev=03 $reg=13 $len=4
215 | save $var=gs3
216 | reuse #GSW04C_refresh $sec=15
217 | reuse #gsw04a_refresh
218 | reuse #gsw04b_refresh
219 | reuse #gsw04d_refresh
220 | reuse #gsw04e_refresh
221 | reuse #gsw04f_refresh
222 | reuse #dnd_send
223 | exit
224 | function GSW04C_btn_6
225 | reuse #bed2_master
226 | load $var=gs3
227 | math.and $hex=FFF3FF
228 | function GSW04C_btn_common
229 | send.modbus $dev=03 $reg=13 $len=4
230 | wait $sec=0.15
231 | load $var=gs3
232 | send.modbus $dev=03 $reg=13 $len=4
233 | reuse #GSW04C_refresh $sec=15
234 | exit
235 | function GSW04C_btn_7
236 | reuse #bed2_relax
237 | load $var=gs3
238 | math.and $hex=FFCFFF
239 | goto #GSW04C_btn_common
240 | function GSW04C_btn_9
241 | reuse #bed2_night
242 | load $var=gs3
243 | math.and $hex=FCFFFF
244 | goto #GSW04C_btn_common
245
246
247
248
249 | function GSW04D_refresh | ok
250 | load $var=workflow
251 | If equal goto #3 $dec=7
252 | load $hex=11440
253 | goto #2
254 | load $hex=11480
255 | save $var=gs4
256 | math.and $hex=10080 //with night light
257 | send.modbus $dev=04 $reg=13 $len=4
258 | exit
259 | function GSW04D_btn_4_dnd
260 | load $hex=11480
261 | send.modbus $dev=04 $reg=13 $len=4
262 | load $var=workflow
263 | If not equal goto #+5 $dec=7
264 | load $dec=0
265 | save $var=workflow
266 | load $hex=11440
267 | goto #+4
268 | load $dec=7
269 | save $var=workflow
270 | load $hex=11480
271 | send.modbus $dev=04 $reg=13 $len=4
272 | save $var=gs4
273 | reuse #GSW04D_refresh $sec=15
274 | reuse #gsw04a_refresh
275 | reuse #gsw04b_refresh
276 | reuse #gsw04c_refresh
277 | reuse #gsw04e_refresh
278 | reuse #gsw04f_refresh
279 | reuse #dnd_send
280 | exit
281 | function GSW04D_btn_6
282 | reuse #bed2_master
283 | load $var=gs4
284 | math.and $hex=FFF3FF
285 | function GSW04D_btn_common
286 | send.modbus $dev=04 $reg=13 $len=4
287 | wait $sec=0.15
288 | load $var=gs4
289 | send.modbus $dev=04 $reg=13 $len=4
290 | reuse #GSW04D_refresh $sec=15
291 | exit
292 | function GSW04D_btn_7
293 | reuse #bed2_relax
294 | load $var=gs4
295 | math.and $hex=FFCFFF
296 | goto #GSW04D_btn_common
297 | function GSW04D_btn_9
298 | reuse #bed2_night
299 | load $var=gs4
300 | math.and $hex=FCFFFF
301 | goto #GSW04D_btn_common
302
303
304
305
306
307
308 | function GSW04E_refresh | ok
309 | load $var=workflow
310 | If equal goto #3 $dec=7
311 | load $hex=11440
312 | goto #2
313 | load $hex=11480
314 | save $var=gs5
315 | math.and $hex=10080 //with night light
316 | send.modbus $dev=05 $reg=13 $len=4
317 | exit
318 | function GSW04E_btn_4_dnd
319 | load $hex=11480
320 | send.modbus $dev=05 $reg=13 $len=4
321 | load $var=workflow
322 | If not equal goto #+5 $dec=7
323 | load $dec=0
324 | save $var=workflow
325 | load $hex=11440
326 | goto #+4
327 | load $dec=7
328 | save $var=workflow
329 | load $hex=11480
330 | send.modbus $dev=05 $reg=13 $len=4
331 | save $var=gs5
332 | reuse #GSW04E_refresh $sec=15
333 | reuse #gsw04a_refresh
334 | reuse #gsw04b_refresh
335 | reuse #gsw04c_refresh
336 | reuse #gsw04d_refresh
337 | reuse #gsw04f_refresh
338 | reuse #dnd_send
339 | exit
340 | function GSW04E_btn_6
341 | reuse #bed3_master
342 | load $var=gs5
343 | math.and $hex=FFF3FF
344 | function GSW04E_btn_common
345 | send.modbus $dev=05 $reg=13 $len=4
346 | wait $sec=0.15
347 | load $var=gs5
348 | send.modbus $dev=05 $reg=13 $len=4
349 | reuse #GSW04E_refresh $sec=15
350 | exit
351 | function GSW04E_btn_7
352 | reuse #bed3_relax
353 | load $var=gs5
354 | math.and $hex=FFCFFF
355 | goto #GSW04E_btn_common
356 | function GSW04E_btn_9
357 | reuse #bed3_night
358 | load $var=gs5
359 | math.and $hex=FCFFFF
360 | goto #GSW04E_btn_common
361
362
363
364
365
366 | function GSW04F_refresh | ok
367 | load $var=workflow
368 | If equal goto #3 $dec=7
369 | load $hex=11440
370 | goto #2
371 | load $hex=11480
372 | save $var=gs6
373 | math.and $hex=10080 //with night light
374 | send.modbus $dev=06 $reg=13 $len=4
375 | exit
376 | function GSW04F_btn_4_dnd
377 | load $hex=11480
378 | send.modbus $dev=06 $reg=13 $len=4
379 | load $var=workflow
380 | If not equal goto #+5 $dec=7
381 | load $dec=0
382 | save $var=workflow
383 | load $hex=11440
384 | goto #+4
385 | load $dec=7
386 | save $var=workflow
387 | load $hex=11480
388 | send.modbus $dev=06 $reg=13 $len=4
389 | save $var=gs6
390 | reuse #GSW04F_refresh $sec=15
391 | reuse #gsw04a_refresh
392 | reuse #gsw04b_refresh
393 | reuse #gsw04c_refresh
394 | reuse #gsw04d_refresh
395 | reuse #gsw04e_refresh
396 | reuse #dnd_send
397 | exit
398 | function GSW04F_btn_6
399 | reuse #bed3_master
400 | load $var=gs6
401 | math.and $hex=FFF3FF
402 | function GSW04F_btn_common
403 | send.modbus $dev=06 $reg=13 $len=4
404 | wait $sec=0.15
405 | load $var=gs6
406 | send.modbus $dev=06 $reg=13 $len=4
407 | reuse #GSW04F_refresh $sec=15
408 | exit
409 | function GSW04F_btn_7
410 | reuse #bed3_relax
411 | load $var=gs6
412 | math.and $hex=FFCFFF
413 | goto #GSW04F_btn_common
414 | function GSW04F_btn_9
415 | reuse #bed3_night
416 | load $var=gs6
417 | math.and $hex=FCFFFF
418 | goto #GSW04F_btn_common
419
420
421
422
423
424
425
426
427 | function GSW03A_refresh | ok
428 | load $bit=11 //night light icon
429 | send.modbus $dev=FE $reg=13 $len=4
430 | exit
431 | function GSW03A_btn_4
432 | reuse #bath2_relax
433 | load $hex=500
434 | function GSW03A_btn_common
435 | send.modbus $dev=FE $reg=13 $len=4
436 | wait $sec=0.15
437 | load $hex=540
438 | send.modbus $dev=FE $reg=13 $len=4
439 | reuse #GSW03A_refresh $sec=15
440 | exit
441 | function GSW03A_btn_5
442 | reuse #bath2_master
443 | load $hex=440
444 | goto #GSW03A_btn_common
445 | function GSW03A_btn_6
446 | reuse #bath2_night
447 | load $hex=140
448 | goto #GSW03A_btn_common
449
450
451
452 | function GSW03B_refresh | ok
453 | load $bit=11 //night light icon
454 | send.modbus $dev=FE $reg=13 $len=4
455 | exit
456 | function GSW03B_btn_4
457 | reuse #bath3_relax
458 | load $hex=500
459 | function GSW03B_btn_common
460 | send.modbus $dev=FE $reg=13 $len=4
461 | wait $sec=0.15
462 | load $hex=540
463 | send.modbus $dev=FE $reg=13 $len=4
464 | reuse #GSW03B_refresh $sec=15
465 | exit
466 | function GSW03B_btn_5
467 | reuse #bath3_master
468 | load $hex=440
469 | goto #GSW03B_btn_common
470 | function GSW03B_btn_6
471 | reuse #bath3_night
472 | load $hex=140
473 | goto #GSW03B_btn_common
474
475
476
477
478 | function GSW03C_refresh | ok
479 | load $bit=11 //night light icon
480 | send.modbus $dev=FE $reg=13 $len=4
481 | exit
482 | function GSW03C_btn_4
483 | reuse #master_bath_relax
484 | load $hex=500
485 | function GSW03C_btn_common
486 | send.modbus $dev=FE $reg=13 $len=4
487 | wait $sec=0.15
488 | load $hex=540
489 | send.modbus $dev=FE $reg=13 $len=4
490 | reuse #GSW03C_refresh $sec=15
491 | exit
492 | function GSW03C_btn_5
493 | reuse #master_bath_master
494 | load $hex=440
495 | goto #GSW03C_btn_common
496 | function GSW03C_btn_6
497 | reuse #master_bath_night
498 | load $hex=140
499 | goto #GSW03C_btn_common
500
501
502
503
504
505 | function GSW02A_refresh | ok
506 | load $dec=0
507 | send.modbus $dev=FE $reg=13 $len=4
508 | exit
509 | function GSW02A_btn_4
510 | reuse #bed2_relax
511 | load $hex=400
512 | function GSW02A_btn_common
513 | send.modbus $dev=FE $reg=13 $len=4
514 | wait $sec=0.15
515 | load $hex=440
516 | send.modbus $dev=FE $reg=13 $len=4
517 | reuse #GSW02A_refresh $sec=15
518 | exit
519 | function GSW02A_btn_6
520 | reuse #bed2_light
521 | load $hex=40
522 | goto #GSW02A_btn_common
523
524
525
526
527
528 | function GSW02B_refresh | ok
529 | load $dec=0
530 | send.modbus $dev=FE $reg=13 $len=4
531 | exit
532 | function GSW02B_btn_4
533 | reuse #bed3_relax
534 | load $hex=400
535 | function GSW02B_btn_common
536 | send.modbus $dev=FE $reg=13 $len=4
537 | wait $sec=0.15
538 | load $hex=440
539 | send.modbus $dev=FE $reg=13 $len=4
540 | reuse #GSW02B_refresh $sec=15
541 | exit
542 | function GSW02B_btn_6
543 | reuse #bed3_light
544 | load $hex=40
545 | goto #GSW02B_btn_common
546
547
548
549
550 | function GSW02C_refresh | ok
551 | load $dec=0
552 | send.modbus $dev=FE $reg=13 $len=4
553 | exit
554 | function GSW02C_btn_4
555 | reuse #master_bed_relax
556 | load $hex=400
557 | function GSW02C_btn_common
558 | send.modbus $dev=FE $reg=13 $len=4
559 | wait $sec=0.15
560 | load $hex=440
561 | send.modbus $dev=FE $reg=13 $len=4
562 | reuse #GSW02C_refresh $sec=15
563 | exit
564 | function GSW02C_btn_6
565 | reuse #master_bed_light
566 | load $hex=40
567 | goto #GSW02C_btn_common
568
569
570
571
572
573 | function GSW01_refresh | ok
574 | load $dec=0
575 | send.modbus $dev=FE $reg=13 $len=4
576 | exit
577 | function GSW01_btn_5
578 | reuse #corridor_light
579 | load $hex=0
580 | send.modbus $dev=FE $reg=13 $len=4
581 | wait $sec=0.15
582 | load $hex=100
583 | send.modbus $dev=FE $reg=13 $len=4
584 | reuse #GSW01_refresh $sec=15
585 | exit
586
587
588
589 | //send modbus
590
591
592 | function dnd_send | ok
593 | load $var=workflow
594 | save modbus $var=m_workflow
595 | exit
596
597
598 | function send_rcu_relays | ok
599 | reuse #use_send_rcu_relays $sec=1
600 | exit
601 | function use_send_rcu_relays
602 | rcu.read relays
603 | save modbus $var=m_rcu_relays
604 | exit
605
606
607
608 | function bed1_master | ok
609 | m_bed1_panel.set $dec=1
610 | exit
611
612
613 | function bed1_relax | ok
614 | m_bed1_panel.set $dec=2
615 | exit
616
617 | function bed1_night | ok
618 | m_bed1_panel.set $dec=3
619 | exit
620
621
622 | function bed2_master | ok
623 | m_bed2_panel.set $dec=1
624 | exit
625
626
627 | function bed2_relax | ok
628 | m_bed2_panel.set $dec=2
629 | exit
630
631
632 | function bed2_night | ok
633 | m_bed2_panel.set $dec=3
634 | exit
635
636
637 | function bed2_light | ok
638 | m_bed2_panel.set $dec=4
639 | exit
640
641
642 | function bed3_master | ok
643 | m_bed3_panel.set $dec=1
644 | exit
645
646
647 | function bed3_relax | ok
648 | m_bed3_panel.set $dec=2
649 | exit
650
651
652 | function bed3_night | ok
653 | m_bed3_panel.set $dec=3
654 | exit
655
656
657 | function bed3_light | ok
658 | m_bed3_panel.set $dec=4
659 | exit
660
661
662 | function master_bed_relax | ok
663 | m_master_bed_panel.set $dec=1
664 | exit
665
666
667 | function master_bed_light | ok
668 | m_master_bed_panel.set $dec=2
669 | exit
670
671
672 | function bath2_relax | ok
673 | m_bath2_panel.set $dec=1
674 | exit
675
676
677 | function bath2_master | ok
678 | m_bath2_panel.set $dec=2
679 | exit
680
681
682 | function bath2_night | ok
683 | m_bath2_panel.set $dec=3
684 | exit
685
686
687
688 | function bath3_relax | ok
689 | m_bath3_panel.set $dec=1
690 | exit
691
692
693 | function bath3_master | ok
694 | m_bath3_panel.set $dec=2
695 | exit
696
697
698 | function bath3_night | ok
699 | m_bath3_panel.set $dec=3
700 | exit
701
702
703
704 | function master_bath_relax | ok
705 | m_master_bath_panel.set $dec=1
706 | exit
707
708
709 | function master_bath_master | ok
710 | m_master_bath_panel.set $dec=2
711 | exit
712
713
714 | function master_bath_night | ok
715 | m_master_bath_panel.set $dec=3
716 | exit
717
718
719 | function corridor_light | ok
720 | rcu.xor $relay=4
721 | goto #send_rcu_relays
722
723
724
725
726
727
728 | //receive modbus
729
730
731 | function modbus_manager
732 | if equal #modbus_user_receive $dec=0
733 | if equal #modbus_workflow_receive $dec=1
734 | if equal #receive_rcu_relays $dec=2
735 | exit
736
737
738 | function modbus_user_receive
739 | load modbus $var=m_user
740 | save $var=user
741 | exit
742
743
744 | function modbus_workflow_receive
745 | load modbus $var=m_workflow
746 | save $var=workflow
747 | function refresh_workflow_panels
748 | reuse #gsw04a_refresh
749 | reuse #gsw04b_refresh
750 | reuse #gsw04c_refresh
751 | reuse #gsw04d_refresh
752 | reuse #gsw04e_refresh
753 | reuse #gsw04f_refresh
754 | exit
755
756
757
758 | function receive_rcu_relays
759 | load modbus $var=m_rcu_relays
760 | rcu.set all relays from acc
761 | exit
762
763
764
765
766
767
768
769
770
771
772

## Program2
| ; |  | Dir: | C:\tini\ModularHotel\ABSlink\RCUmanager\bin\Release
| ;code |  | # | Description | done | Parameters (8 bytes)
0000 | 19 00 00 00 00 00 00 00; | #startup | 0x01 | GoTo & Wait | d | 0x01 | wait # tick |  | 2bytete optional goto |  |  | tick | [5 empty] | 00=nogoto 00=nowait
0001 | 00 00 00 00 09 2E ED 09; | version [35561452341814213551145390817034,9] |  |  | d | 0x03 | WaitTick/OrigDev |  | 2byte goto (acc->acc called) |  |  | tick | Relative, reuse of existing task with same device if present updating tick (used for timeout interactive mode) [multidev]
0002 | 01 01 20 00 00 00 00 00; | goto #debugging | 0x0a | Wait absolute | d | 1=value,3=1B,4=2B, 5=4B,a=acc[0]=RTC(add), |  |  |  |  | 2 byte empty |  |  |  | 4 byte value |  | 3-5= addr a-b uses RTC+acc[0]
0003 | 01 01 00 00 00 00 00 00; | reserved for ipad | 0x02 | Rcu Hardware | d | 0x01 | set relay |  | 0=accum, 1=value, 3=add1B, 4=add2B, 5=add4B | [5 empty] | byte low bitmap from relay 1 to 8
0004 | 01 01 00 00 00 00 00 00; | reserved for ipad |  |  | d | 0x02 | unset relay |  | 0=accum, 1=value, 3=add1B, 4=add2B, 5=add4B | [5 empty] | byte low bitmap from relay 1 to 8
0005 | 01 01 00 00 00 00 00 00; | reserved for ipad |  |  | d | 0x03 | read relays in accumulator
0006 | 01 01 00 00 00 00 00 00; | reserved for ipad |  |  | d | 0x04 | set all relays |  | 0=accum, 1=value, 3=add1B, 4=add2B, 5=add4B | [5 empty] | bitmap
0007 | 01 01 00 00 00 00 00 00; | reserved for ipad |  |  | d | 0x05 | set OUT Lock % |  | 0=accum, 1=value, 3=add1B, 4=add2B, 5=add4B | [5 empty] | 50% = 12Volt
0008 | 01 01 00 00 00 00 00 00; | reserved for ipad |  |  | d | 0x06 | set 0-10 V [1] |  | 0=accum, 1=value, 3=add1B, 4=add2B, 5=add4B
0009 | 01 01 00 00 00 00 00 00; | reserved for ipad |  |  | d | 0x07 | set 0-10 V [2] |  | 0=accum, 1=value, 3=add1B, 4=add2B, 5=add4B
000A | 01 01 00 00 00 00 00 00; | reserved for ipad |  |  |  | 0x08 | Input->Accumulator |  | Input # |  |  | Get inputs value in accumulator, if par1=0 all inputs (bitmap)
000B | 01 01 00 00 00 00 00 00; | reserved for ipad |  |  | d | 0x09 | set on relays |  | 0=accum, 1=value, 3=add1B, 4=add2B, 5=add4B | [5 empty] | bitmap
000C | 01 01 00 00 00 00 00 00; | reserved for ipad |  |  | d | 0x0a | set off relays |  | 0=accum, 1=value, 3=add1B, 4=add2B, 5=add4B | [5 empty] | bitmap
000D | 01 01 00 00 00 00 00 00; | reserved for ipad |  |  | d | 0x0b | xor relays |  | 0=accum, 1=value, 3=add1B, 4=add2B, 5=add4B | [5 empty] | bitmap
000E | 01 01 00 00 00 00 00 00; | reserved for ipad | 0x03 | Run task | d | 0x01 | NewTask Wait # tick |  | 2byte goto |  |  | tick | Run a separate thread
000F | 01 01 00 00 00 00 00 00; | reserved for ipad |  |  | d | 0x02 | Reuse Wait # tick |  | 2byte goto (acc->acc called) |  |  | tick | Relative, reuse of existing task if present updating tick (used for timeout interactive mode)
0010 | 01 01 00 00 00 00 00 00; | reserved for ipad |  |  | d | 0x03 | Reuse/WaitTick/OrigDev |  | 2byte goto (acc->acc called) |  |  | tick | Relative, reuse of existing task with same device if present updating tick (used for timeout interactive mode) [multidev]
0011 | 01 01 00 00 00 00 00 00; | reserved for ipad | 0x04 | Exit | d | 0x01 | Stop execution
0012 | 01 01 00 00 00 00 00 00; | reserved for ipad |  |  |  | 0x02 | Return to caller in accumulator
0013 | 01 01 00 00 00 00 00 00; | reserved for ipad | 0x05 | GoTo if acc[0] != | d |  | 0=acc, 1=value, 3=addr 1B, 4=addr 2B, 5=addr 4B | [6 empty] | 2byte goto |  | 4bytes value
0014 | 01 01 00 00 00 00 00 00; | reserved for ipad | 0x06 | GoTo if acc[0] > | d |  | 0=acc, 1=value, 3=addr 1B, 4=addr 2B, 5=addr 4B | [6 empty] | 2byte goto |  | 4bytes value
0015 | 01 01 00 00 00 00 00 00; | reserved for ipad | 0x07 | GoTo if acc[0] < | d |  | 0=acc, 1=value, 3=addr 1B, 4=addr 2B, 5=addr 4B | [6 empty] | 2byte goto |  | 4bytes value
0016 | 01 01 00 00 00 00 00 00; | reserved for ipad | 0x08 | GoTo if acc[0] = | d |  | 0=acc, 1=value, 3=addr 1B, 4=addr 2B, 5=addr 4B | [6 empty] | 2byte goto |  | 4bytes value
0017 | 01 01 22 00 00 00 00 00; | goto #checkout | 0x09 | GoTo if acc[0] AND | d |  | 0=acc, 1=value, 3=addr 1B, 4=addr 2B, 5=addr 4B | [6 empty] | 2byte goto |  | 4bytes value |  |  | goto if a bit match
0018 | 01 01 23 00 00 00 00 00; | goto #checkin | 0x10 | Mathematics | d | 0x01 | Add | 1=value, 2=RPN, 3=addr 1B, 4=addr 2B, 5=addr 4B | [5 empty] | empty | 4 byte value |  | 1 value is from last 4 bytes
0019 | 21 06 00 0F 03 20 00 00; | send.modbus $type=gsw $reg=15 $dec=80*10 |  |  | d | 0x02 | Sub | 1=value, 2=RPN, 3=addr 1B, 4=addr 2B, 5=addr 4B | [5 empty] | empty | 4 byte value |  | 2 RPN operates in Accumulator and last stack, shift down 3 values in stack
001A | 21 06 00 10 01 2C 00 00; | send.modbus $type=gsw $reg=16 $dec=30*10 |  |  | d | 0x03 | Mul | 1=value, 2=RPN, 3=addr 1B, 4=addr 2B, 5=addr 4B | [5 empty] | empty | 4 byte value |  | 3-5 uses memory with 1,2,4 bytes
001B | 03 02 FC 01 50 C3 00 00; | reuse #refresh_workflow_panels $sec=5 |  |  | d | 0x04 | OR | 1=value, 2=RPN, 3=addr 1B, 4=addr 2B, 5=addr 4B | [5 empty] | empty | 4 byte value
001C | 01 01 00 00 50 C3 00 00; | wait $sec=5 |  |  | d | 0x05 | XOR | 1=value, 2=RPN, 3=addr 1B, 4=addr 2B, 5=addr 4B | [5 empty] | empty | 4 byte value |  | Stack is 3 values + Accumulator like Forth
001D | 10 80 01 00 00 00 00 00; | load $dec=0 |  |  | d | 0x06 | AND | 1=value, 2=RPN, 3=addr 1B, 4=addr 2B, 5=addr 4B | [5 empty] | empty | 4 byte value
001E | 10 81 12 00 0A 00 00 00; | save modbus $var=m_notify |  |  | d | 0x07 | << | 1=value, 2=RPN, 3=addr 1B, 4=addr 2B, 5=addr 4B | [5 empty] | empty | 4 byte value
001F | 04 01 00 00 00 00 00 00; | exit |  |  | d | 0x08 | >> | 1=value, 2=RPN, 3=addr 1B, 4=addr 2B, 5=addr 4B | [5 empty] | empty | 4 byte value |  |  | 1B=byte, 2B=16bit, 4B=32bit
0020 | 40 01 01 00 00 00 00 00; | debug |  |  | d | 0x09 | Div | 0=Acc, 1=value, 2=RPN, 3=addr 1B, 4=addr 2B, 5=addr 4B | [5 empty] | empty | 4 byte value |  | 3-5 uses memory with 1,2,4 bytes
0021 | 04 01 00 00 00 00 00 00; | exit |  |  | d | 0x0a | Mod | 0=Acc, 1=value, 2=RPN, 3=addr 1B, 4=addr 2B, 5=addr 4B | [5 empty] | empty | 4 byte value |  | 3-5 uses memory with 1,2,4 bytes
0022 | 04 01 00 00 00 00 00 00; | exit |  |  | d | 0x80 | PUSH | 1=value,3=1B,4=2B, 5=4B,a=acc[0]=RTC(add), | [5 empty] | shiftYN | 4 byte value |  | 3-5= addr a-b uses RTC+acc[0]
0023 | 01 01 22 00 00 00 00 00; | goto #checkout |  |  | d | [8 empty] | shiftYN | 1 item size |  | 1 byte relative positive address, 1 elements, 1 empty
0024 | 04 01 00 00 00 00 00 00; | exit |  |  | d | [8 empty] | shiftYN | 1 item size |  | 1 byte relative positive address, 1 elements, 1 empty
0025 | 10 80 0A 00 16 00 00 00; | load $var=workflow |  |  | d |  |  | e=CurrentEventDevice, f=addr 4B+OrigDevEnum(DeviceMap) | [5 empty] | shiftYN | 4 byte value
0026 | 08 01 29 00 07 00 00 00; | if equal goto #3 $dec=7 |  |  | d | 0x81 | POP | 3=1B,4=2B,5=4B,a=RTC(add)=acc[0],b=RTC(acc[0])=acc[1] | [5 empty] | shiftYN | 4 byte value
0027 | 10 80 01 00 40 14 01 00; | load $hex=11440 |  |  | d |  |  | e=CurrentEventDevice, f=addr 4B+OrigDevEnum(DeviceMap) | [5 empty] | shiftYN | 4 byte value
0028 | 01 01 2A 00 00 00 00 00; | goto #2 |  |  | d | 0x82 | PUSH time | [6 empty] | shiftYN
0029 | 10 80 01 00 80 14 01 00; | load $hex=11480 | 0x20 | Send ModBus 1 Word | d | Dest | PosHi | PosLo | Whi | Wlo | crcH | crcL |  | Dest FF=ServerIP, FE=OrigDevice |  |  |  |  | # dev map (Type=all devices with specified type)
002A | 10 81 0A 00 17 00 00 00; | save $var=gs1 | 0x21 | Send ModBus 1 Word | d | Type | PosHi | PosLo | Whi | Wlo | crcH | crcL |  | Dest FF=ServerIP, FE=OrigDevice |  |  |  |  | Send to all devices with type=x
002B | 10 06 01 00 80 00 01 00; | math.and $hex=10080 | 0x22 | Send ModBus Accumulator | d | Dest | PosHi | PosLo | bytes(2-16),NW |  | crcH | crcL |  | Dest FF=ServerIP, FE=OrigDevice |  |  |  |  | NW=no wait
002C | 22 01 00 0D 04 00 00 00; | send.modbus $dev=01 $reg=13 $len=4 | 0x23 | Send ModBus Accumulator | d | Type | PosHi | PosLo | bytes(2-16),00 |  | crcH | crcL |  | Dest FF=ServerIP, FE=OrigDevice |  |  |  |  | Send to all devices with type=x
002D | 04 01 00 00 00 00 00 00; | exit | 0x26 | Read modbus in Accumulator | d | Dest | PosHi | PosLo | bytes(2,4), 00 |  | crcH | crcL |  | Dest FF=ServerIP, FE=OrigDevice
002E | 10 80 01 00 80 14 01 00; | load $hex=11480 | 0x2a | Seand modbus Acc[*] | d d d: d; PUSH time Whi Whi: Dest+PosH+PosL+Len (1b+1b+1b+1b+max 12b max message) |  | gateway |  | 02190003;c8 TAG SetPoint=200 ->35192835;200;0;0
002F | 22 01 00 0D 04 00 00 00; | send.modbus $dev=01 $reg=13 $len=4 | 0x2b | Read modbus Acc[0]->Acc[*] | d d d: d; PUSH time Whi Whi: Dest+PosH+PosL+Len |  | gateway |  | Reat TAG Setpoint 35192835;0;0;0
0030 | 10 80 0A 00 16 00 00 00; | load $var=workflow | 0x30 | Call RCU Acc[*] | 0x82 Dest Type: Dest; PUSH time Whi Whi: Program address |  | Pass 4 register to the defined RCU device (+read ModBus 3 su TCP/IP)
0031 | 05 01 36 00 07 00 00 00; | if not equal goto #+5 $dec=7
0032 | 10 80 01 00 00 00 00 00; | load $dec=0 | # | Notify packet | d d d: Parameters
0033 | 10 81 0A 00 16 00 00 00; | save $var=workflow | 1 | Eartbeat | d d d: Counter
0034 | 10 80 01 00 40 14 01 00; | load $hex=11440 | 2 | Card Insert | d d d: CardId (8), Time
0035 | 01 01 39 00 00 00 00 00; | goto #+4 | 3 | CardExtract | d d d: none
0036 | 10 80 01 00 07 00 00 00; | load $dec=7 | 4 | Mur/Dnd | d d d: Status
0037 | 10 81 0A 00 16 00 00 00; | save $var=workflow | 5 | OpenNOK | d d d: Status, Time
0038 | 10 80 01 00 80 14 01 00; | load $hex=11480 | 6 | Open OK | d d d: CardId (8), Time
0039 | 22 01 00 0D 04 00 00 00; | send.modbus $dev=01 $reg=13 $len=4 | 7 | Read RTC Var | bar: d d d to PUSH time PosLo PosLo
003A | 10 81 0A 00 17 00 00 00; | save $var=gs1 | 8 | Read modbus from device | bar: d d d to PUSH time PosLo PosLo
003B | 03 02 25 00 F0 49 02 00; | reuse #gsw04a_refresh $sec=15 | bar: d d d to PUSH time PosLo PosLo
003C | 03 02 54 00 00 00 00 00; | reuse #gsw04b_refresh | bar: d d d to PUSH time PosLo PosLo
003D | 03 02 83 00 00 00 00 00; | reuse #gsw04c_refresh | bar: d d d to PUSH time PosLo PosLo
003E | 03 02 B2 00 00 00 00 00; | reuse #gsw04d_refresh
003F | 03 02 E1 00 00 00 00 00; | reuse #gsw04e_refresh
0040 | 03 02 10 01 00 00 00 00; | reuse #gsw04f_refresh
0041 | 03 02 A7 01 00 00 00 00; | reuse #dnd_send
0042 | 04 01 00 00 00 00 00 00; | exit
0043 | 03 02 AF 01 00 00 00 00; | reuse #bed1_master
0044 | 10 80 0A 00 17 00 00 00; | load $var=gs1
0045 | 10 06 01 00 FF F3 FF 00; | math.and $hex=fff3ff
0046 | 22 01 00 0D 04 00 00 00; | send.modbus $dev=01 $reg=13 $len=4
0047 | 01 01 00 00 DC 05 00 00; | wait $sec=0.15
0048 | 10 80 0A 00 17 00 00 00; | load $var=gs1
0049 | 22 01 00 0D 04 00 00 00; | send.modbus $dev=01 $reg=13 $len=4
004A | 03 02 25 00 F0 49 02 00; | reuse #gsw04a_refresh $sec=15
004B | 04 01 00 00 00 00 00 00; | exit
004C | 03 02 B2 01 00 00 00 00; | reuse #bed1_relax
004D | 10 80 0A 00 17 00 00 00; | load $var=gs1
004E | 10 06 01 00 FF CF FF 00; | math.and $hex=ffcfff
004F | 01 01 46 00 00 00 00 00; | goto #gsw04a_btn_common
0050 | 03 02 B5 01 00 00 00 00; | reuse #bed1_night
0051 | 10 80 0A 00 17 00 00 00; | load $var=gs1
0052 | 10 06 01 00 FF FF FC 00; | math.and $hex=fcffff
0053 | 01 01 46 00 00 00 00 00; | goto #gsw04a_btn_common
0054 | 10 80 0A 00 16 00 00 00; | load $var=workflow
0055 | 08 01 58 00 07 00 00 00; | if equal goto #3 $dec=7
0056 | 10 80 01 00 40 14 01 00; | load $hex=11440
0057 | 01 01 59 00 00 00 00 00; | goto #2
0058 | 10 80 01 00 80 14 01 00; | load $hex=11480
0059 | 10 81 0A 00 18 00 00 00; | save $var=gs2
005A | 10 06 01 00 80 00 01 00; | math.and $hex=10080
005B | 22 02 00 0D 04 00 00 00; | send.modbus $dev=02 $reg=13 $len=4
005C | 04 01 00 00 00 00 00 00; | exit
005D | 10 80 01 00 80 14 01 00; | load $hex=11480
005E | 22 02 00 0D 04 00 00 00; | send.modbus $dev=02 $reg=13 $len=4
005F | 10 80 0A 00 16 00 00 00; | load $var=workflow
0060 | 05 01 65 00 07 00 00 00; | if not equal goto #+5 $dec=7
0061 | 10 80 01 00 00 00 00 00; | load $dec=0
0062 | 10 81 0A 00 16 00 00 00; | save $var=workflow
0063 | 10 80 01 00 40 14 01 00; | load $hex=11440
0064 | 01 01 68 00 00 00 00 00; | goto #+4
0065 | 10 80 01 00 07 00 00 00; | load $dec=7
0066 | 10 81 0A 00 16 00 00 00; | save $var=workflow
0067 | 10 80 01 00 80 14 01 00; | load $hex=11480
0068 | 22 02 00 0D 04 00 00 00; | send.modbus $dev=02 $reg=13 $len=4
0069 | 10 81 0A 00 18 00 00 00; | save $var=gs2
006A | 03 02 54 00 F0 49 02 00; | reuse #gsw04b_refresh $sec=15
006B | 03 02 25 00 00 00 00 00; | reuse #gsw04a_refresh
006C | 03 02 83 00 00 00 00 00; | reuse #gsw04c_refresh
006D | 03 02 B2 00 00 00 00 00; | reuse #gsw04d_refresh
006E | 03 02 E1 00 00 00 00 00; | reuse #gsw04e_refresh
006F | 03 02 10 01 00 00 00 00; | reuse #gsw04f_refresh
0070 | 03 02 A7 01 00 00 00 00; | reuse #dnd_send
0071 | 04 01 00 00 00 00 00 00; | exit
0072 | 03 02 AF 01 00 00 00 00; | reuse #bed1_master
0073 | 10 80 0A 00 18 00 00 00; | load $var=gs2
0074 | 10 06 01 00 FF F3 FF 00; | math.and $hex=fff3ff
0075 | 22 02 00 0D 04 00 00 00; | send.modbus $dev=02 $reg=13 $len=4
0076 | 01 01 00 00 DC 05 00 00; | wait $sec=0.15
0077 | 10 80 0A 00 18 00 00 00; | load $var=gs2
0078 | 22 02 00 0D 04 00 00 00; | send.modbus $dev=02 $reg=13 $len=4
0079 | 03 02 54 00 F0 49 02 00; | reuse #gsw04b_refresh $sec=15
007A | 04 01 00 00 00 00 00 00; | exit
007B | 03 02 B2 01 00 00 00 00; | reuse #bed1_relax
007C | 10 80 0A 00 18 00 00 00; | load $var=gs2
007D | 10 06 01 00 FF CF FF 00; | math.and $hex=ffcfff
007E | 01 01 75 00 00 00 00 00; | goto #gsw04b_btn_common
007F | 03 02 B5 01 00 00 00 00; | reuse #bed1_night
0080 | 10 80 0A 00 18 00 00 00; | load $var=gs2
0081 | 10 06 01 00 FF FF FC 00; | math.and $hex=fcffff
0082 | 01 01 75 00 00 00 00 00; | goto #gsw04b_btn_common
0083 | 10 80 0A 00 16 00 00 00; | load $var=workflow
0084 | 08 01 87 00 07 00 00 00; | if equal goto #3 $dec=7
0085 | 10 80 01 00 40 14 01 00; | load $hex=11440
0086 | 01 01 88 00 00 00 00 00; | goto #2
0087 | 10 80 01 00 80 14 01 00; | load $hex=11480
0088 | 10 81 0A 00 19 00 00 00; | save $var=gs3
0089 | 10 06 01 00 80 00 01 00; | math.and $hex=10080
008A | 22 03 00 0D 04 00 00 00; | send.modbus $dev=03 $reg=13 $len=4
008B | 04 01 00 00 00 00 00 00; | exit
008C | 10 80 01 00 80 14 01 00; | load $hex=11480
008D | 22 03 00 0D 04 00 00 00; | send.modbus $dev=03 $reg=13 $len=4
008E | 10 80 0A 00 16 00 00 00; | load $var=workflow
008F | 05 01 94 00 07 00 00 00; | if not equal goto #+5 $dec=7
0090 | 10 80 01 00 00 00 00 00; | load $dec=0
0091 | 10 81 0A 00 16 00 00 00; | save $var=workflow
0092 | 10 80 01 00 40 14 01 00; | load $hex=11440
0093 | 01 01 97 00 00 00 00 00; | goto #4
0094 | 10 80 01 00 07 00 00 00; | load $dec=7
0095 | 10 81 0A 00 16 00 00 00; | save $var=workflow
0096 | 10 80 01 00 80 14 01 00; | load $hex=11480
0097 | 22 03 00 0D 04 00 00 00; | send.modbus $dev=03 $reg=13 $len=4
0098 | 10 81 0A 00 19 00 00 00; | save $var=gs3
0099 | 03 02 83 00 F0 49 02 00; | reuse #gsw04c_refresh $sec=15
009A | 03 02 25 00 00 00 00 00; | reuse #gsw04a_refresh
009B | 03 02 54 00 00 00 00 00; | reuse #gsw04b_refresh
009C | 03 02 B2 00 00 00 00 00; | reuse #gsw04d_refresh
009D | 03 02 E1 00 00 00 00 00; | reuse #gsw04e_refresh
009E | 03 02 10 01 00 00 00 00; | reuse #gsw04f_refresh
009F | 03 02 A7 01 00 00 00 00; | reuse #dnd_send
00A0 | 04 01 00 00 00 00 00 00; | exit
00A1 | 03 02 B8 01 00 00 00 00; | reuse #bed2_master
00A2 | 10 80 0A 00 19 00 00 00; | load $var=gs3
00A3 | 10 06 01 00 FF F3 FF 00; | math.and $hex=fff3ff
00A4 | 22 03 00 0D 04 00 00 00; | send.modbus $dev=03 $reg=13 $len=4
00A5 | 01 01 00 00 DC 05 00 00; | wait $sec=0.15
00A6 | 10 80 0A 00 19 00 00 00; | load $var=gs3
00A7 | 22 03 00 0D 04 00 00 00; | send.modbus $dev=03 $reg=13 $len=4
00A8 | 03 02 83 00 F0 49 02 00; | reuse #gsw04c_refresh $sec=15
00A9 | 04 01 00 00 00 00 00 00; | exit
00AA | 03 02 BB 01 00 00 00 00; | reuse #bed2_relax
00AB | 10 80 0A 00 19 00 00 00; | load $var=gs3
00AC | 10 06 01 00 FF CF FF 00; | math.and $hex=ffcfff
00AD | 01 01 A4 00 00 00 00 00; | goto #gsw04c_btn_common
00AE | 03 02 BE 01 00 00 00 00; | reuse #bed2_night
00AF | 10 80 0A 00 19 00 00 00; | load $var=gs3
00B0 | 10 06 01 00 FF FF FC 00; | math.and $hex=fcffff
00B1 | 01 01 A4 00 00 00 00 00; | goto #gsw04c_btn_common
00B2 | 10 80 0A 00 16 00 00 00; | load $var=workflow
00B3 | 08 01 B6 00 07 00 00 00; | if equal goto #3 $dec=7
00B4 | 10 80 01 00 40 14 01 00; | load $hex=11440
00B5 | 01 01 B7 00 00 00 00 00; | goto #2
00B6 | 10 80 01 00 80 14 01 00; | load $hex=11480
00B7 | 10 81 0A 00 1A 00 00 00; | save $var=gs4
00B8 | 10 06 01 00 80 00 01 00; | math.and $hex=10080
00B9 | 22 04 00 0D 04 00 00 00; | send.modbus $dev=04 $reg=13 $len=4
00BA | 04 01 00 00 00 00 00 00; | exit
00BB | 10 80 01 00 80 14 01 00; | load $hex=11480
00BC | 22 04 00 0D 04 00 00 00; | send.modbus $dev=04 $reg=13 $len=4
00BD | 10 80 0A 00 16 00 00 00; | load $var=workflow
00BE | 05 01 C3 00 07 00 00 00; | if not equal goto #+5 $dec=7
00BF | 10 80 01 00 00 00 00 00; | load $dec=0
00C0 | 10 81 0A 00 16 00 00 00; | save $var=workflow
00C1 | 10 80 01 00 40 14 01 00; | load $hex=11440
00C2 | 01 01 C6 00 00 00 00 00; | goto #+4
00C3 | 10 80 01 00 07 00 00 00; | load $dec=7
00C4 | 10 81 0A 00 16 00 00 00; | save $var=workflow
00C5 | 10 80 01 00 80 14 01 00; | load $hex=11480
00C6 | 22 04 00 0D 04 00 00 00; | send.modbus $dev=04 $reg=13 $len=4
00C7 | 10 81 0A 00 1A 00 00 00; | save $var=gs4
00C8 | 03 02 B2 00 F0 49 02 00; | reuse #gsw04d_refresh $sec=15
00C9 | 03 02 25 00 00 00 00 00; | reuse #gsw04a_refresh
00CA | 03 02 54 00 00 00 00 00; | reuse #gsw04b_refresh
00CB | 03 02 83 00 00 00 00 00; | reuse #gsw04c_refresh
00CC | 03 02 E1 00 00 00 00 00; | reuse #gsw04e_refresh
00CD | 03 02 10 01 00 00 00 00; | reuse #gsw04f_refresh
00CE | 03 02 A7 01 00 00 00 00; | reuse #dnd_send
00CF | 04 01 00 00 00 00 00 00; | exit
00D0 | 03 02 B8 01 00 00 00 00; | reuse #bed2_master
00D1 | 10 80 0A 00 1A 00 00 00; | load $var=gs4
00D2 | 10 06 01 00 FF F3 FF 00; | math.and $hex=fff3ff
00D3 | 22 04 00 0D 04 00 00 00; | send.modbus $dev=04 $reg=13 $len=4
00D4 | 01 01 00 00 DC 05 00 00; | wait $sec=0.15
00D5 | 10 80 0A 00 1A 00 00 00; | load $var=gs4
00D6 | 22 04 00 0D 04 00 00 00; | send.modbus $dev=04 $reg=13 $len=4
00D7 | 03 02 B2 00 F0 49 02 00; | reuse #gsw04d_refresh $sec=15
00D8 | 04 01 00 00 00 00 00 00; | exit
00D9 | 03 02 BB 01 00 00 00 00; | reuse #bed2_relax
00DA | 10 80 0A 00 1A 00 00 00; | load $var=gs4
00DB | 10 06 01 00 FF CF FF 00; | math.and $hex=ffcfff
00DC | 01 01 D3 00 00 00 00 00; | goto #gsw04d_btn_common
00DD | 03 02 BE 01 00 00 00 00; | reuse #bed2_night
00DE | 10 80 0A 00 1A 00 00 00; | load $var=gs4
00DF | 10 06 01 00 FF FF FC 00; | math.and $hex=fcffff
00E0 | 01 01 D3 00 00 00 00 00; | goto #gsw04d_btn_common
00E1 | 10 80 0A 00 16 00 00 00; | load $var=workflow
00E2 | 08 01 E5 00 07 00 00 00; | if equal goto #3 $dec=7
00E3 | 10 80 01 00 40 14 01 00; | load $hex=11440
00E4 | 01 01 E6 00 00 00 00 00; | goto #2
00E5 | 10 80 01 00 80 14 01 00; | load $hex=11480
00E6 | 10 81 0A 00 1B 00 00 00; | save $var=gs5
00E7 | 10 06 01 00 80 00 01 00; | math.and $hex=10080
00E8 | 22 05 00 0D 04 00 00 00; | send.modbus $dev=05 $reg=13 $len=4
00E9 | 04 01 00 00 00 00 00 00; | exit
00EA | 10 80 01 00 80 14 01 00; | load $hex=11480
00EB | 22 05 00 0D 04 00 00 00; | send.modbus $dev=05 $reg=13 $len=4
00EC | 10 80 0A 00 16 00 00 00; | load $var=workflow
00ED | 05 01 F2 00 07 00 00 00; | if not equal goto #+5 $dec=7
00EE | 10 80 01 00 00 00 00 00; | load $dec=0
00EF | 10 81 0A 00 16 00 00 00; | save $var=workflow
00F0 | 10 80 01 00 40 14 01 00; | load $hex=11440
00F1 | 01 01 F5 00 00 00 00 00; | goto #+4
00F2 | 10 80 01 00 07 00 00 00; | load $dec=7
00F3 | 10 81 0A 00 16 00 00 00; | save $var=workflow
00F4 | 10 80 01 00 80 14 01 00; | load $hex=11480
00F5 | 22 05 00 0D 04 00 00 00; | send.modbus $dev=05 $reg=13 $len=4
00F6 | 10 81 0A 00 1B 00 00 00; | save $var=gs5
00F7 | 03 02 E1 00 F0 49 02 00; | reuse #gsw04e_refresh $sec=15
00F8 | 03 02 25 00 00 00 00 00; | reuse #gsw04a_refresh
00F9 | 03 02 54 00 00 00 00 00; | reuse #gsw04b_refresh
00FA | 03 02 83 00 00 00 00 00; | reuse #gsw04c_refresh
00FB | 03 02 B2 00 00 00 00 00; | reuse #gsw04d_refresh
00FC | 03 02 10 01 00 00 00 00; | reuse #gsw04f_refresh
00FD | 03 02 A7 01 00 00 00 00; | reuse #dnd_send
00FE | 04 01 00 00 00 00 00 00; | exit
00FF | 03 02 C4 01 00 00 00 00; | reuse #bed3_master
0100 | 10 80 0A 00 1B 00 00 00; | load $var=gs5
0101 | 10 06 01 00 FF F3 FF 00; | math.and $hex=fff3ff
0102 | 22 05 00 0D 04 00 00 00; | send.modbus $dev=05 $reg=13 $len=4
0103 | 01 01 00 00 DC 05 00 00; | wait $sec=0.15
0104 | 10 80 0A 00 1B 00 00 00; | load $var=gs5
0105 | 22 05 00 0D 04 00 00 00; | send.modbus $dev=05 $reg=13 $len=4
0106 | 03 02 E1 00 F0 49 02 00; | reuse #gsw04e_refresh $sec=15
0107 | 04 01 00 00 00 00 00 00; | exit
0108 | 03 02 C7 01 00 00 00 00; | reuse #bed3_relax
0109 | 10 80 0A 00 1B 00 00 00; | load $var=gs5
010A | 10 06 01 00 FF CF FF 00; | math.and $hex=ffcfff
010B | 01 01 02 01 00 00 00 00; | goto #gsw04e_btn_common
010C | 03 02 CA 01 00 00 00 00; | reuse #bed3_night
010D | 10 80 0A 00 1B 00 00 00; | load $var=gs5
010E | 10 06 01 00 FF FF FC 00; | math.and $hex=fcffff
010F | 01 01 02 01 00 00 00 00; | goto #gsw04e_btn_common
0110 | 10 80 0A 00 16 00 00 00; | load $var=workflow
0111 | 08 01 14 01 07 00 00 00; | if equal goto #3 $dec=7
0112 | 10 80 01 00 40 14 01 00; | load $hex=11440
0113 | 01 01 15 01 00 00 00 00; | goto #2
0114 | 10 80 01 00 80 14 01 00; | load $hex=11480
0115 | 10 81 0A 00 1C 00 00 00; | save $var=gs6
0116 | 10 06 01 00 80 00 01 00; | math.and $hex=10080
0117 | 22 06 00 0D 04 00 00 00; | send.modbus $dev=06 $reg=13 $len=4
0118 | 04 01 00 00 00 00 00 00; | exit
0119 | 10 80 01 00 80 14 01 00; | load $hex=11480
011A | 22 06 00 0D 04 00 00 00; | send.modbus $dev=06 $reg=13 $len=4
011B | 10 80 0A 00 16 00 00 00; | load $var=workflow
011C | 05 01 21 01 07 00 00 00; | if not equal goto #+5 $dec=7
011D | 10 80 01 00 00 00 00 00; | load $dec=0
011E | 10 81 0A 00 16 00 00 00; | save $var=workflow
011F | 10 80 01 00 40 14 01 00; | load $hex=11440
0120 | 01 01 24 01 00 00 00 00; | goto #+4
0121 | 10 80 01 00 07 00 00 00; | load $dec=7
0122 | 10 81 0A 00 16 00 00 00; | save $var=workflow
0123 | 10 80 01 00 80 14 01 00; | load $hex=11480
0124 | 22 06 00 0D 04 00 00 00; | send.modbus $dev=06 $reg=13 $len=4
0125 | 10 81 0A 00 1C 00 00 00; | save $var=gs6
0126 | 03 02 10 01 F0 49 02 00; | reuse #gsw04f_refresh $sec=15
0127 | 03 02 25 00 00 00 00 00; | reuse #gsw04a_refresh
0128 | 03 02 54 00 00 00 00 00; | reuse #gsw04b_refresh
0129 | 03 02 83 00 00 00 00 00; | reuse #gsw04c_refresh
012A | 03 02 B2 00 00 00 00 00; | reuse #gsw04d_refresh
012B | 03 02 E1 00 00 00 00 00; | reuse #gsw04e_refresh
012C | 03 02 A7 01 00 00 00 00; | reuse #dnd_send
012D | 04 01 00 00 00 00 00 00; | exit
012E | 03 02 C4 01 00 00 00 00; | reuse #bed3_master
012F | 10 80 0A 00 1C 00 00 00; | load $var=gs6
0130 | 10 06 01 00 FF F3 FF 00; | math.and $hex=fff3ff
0131 | 22 06 00 0D 04 00 00 00; | send.modbus $dev=06 $reg=13 $len=4
0132 | 01 01 00 00 DC 05 00 00; | wait $sec=0.15
0133 | 10 80 0A 00 1C 00 00 00; | load $var=gs6
0134 | 22 06 00 0D 04 00 00 00; | send.modbus $dev=06 $reg=13 $len=4
0135 | 03 02 10 01 F0 49 02 00; | reuse #gsw04f_refresh $sec=15
0136 | 04 01 00 00 00 00 00 00; | exit
0137 | 03 02 C7 01 00 00 00 00; | reuse #bed3_relax
0138 | 10 80 0A 00 1C 00 00 00; | load $var=gs6
0139 | 10 06 01 00 FF CF FF 00; | math.and $hex=ffcfff
013A | 01 01 31 01 00 00 00 00; | goto #gsw04f_btn_common
013B | 03 02 CA 01 00 00 00 00; | reuse #bed3_night
013C | 10 80 0A 00 1C 00 00 00; | load $var=gs6
013D | 10 06 01 00 FF FF FC 00; | math.and $hex=fcffff
013E | 01 01 31 01 00 00 00 00; | goto #gsw04f_btn_common
013F | 10 80 01 00 00 04 00 00; | load $bit=11
0140 | 22 FE 00 0D 04 00 00 00; | send.modbus $dev=fe $reg=13 $len=4
0141 | 04 01 00 00 00 00 00 00; | exit
0142 | 03 02 D6 01 00 00 00 00; | reuse #bath2_relax
0143 | 10 80 01 00 00 05 00 00; | load $hex=500
0144 | 22 FE 00 0D 04 00 00 00; | send.modbus $dev=fe $reg=13 $len=4
0145 | 01 01 00 00 DC 05 00 00; | wait $sec=0.15
0146 | 10 80 01 00 40 05 00 00; | load $hex=540
0147 | 22 FE 00 0D 04 00 00 00; | send.modbus $dev=fe $reg=13 $len=4
0148 | 03 02 3F 01 F0 49 02 00; | reuse #gsw03a_refresh $sec=15
0149 | 04 01 00 00 00 00 00 00; | exit
014A | 03 02 D9 01 00 00 00 00; | reuse #bath2_master
014B | 10 80 01 00 40 04 00 00; | load $hex=440
014C | 01 01 44 01 00 00 00 00; | goto #gsw03a_btn_common
014D | 03 02 DC 01 00 00 00 00; | reuse #bath2_night
014E | 10 80 01 00 40 01 00 00; | load $hex=140
014F | 01 01 44 01 00 00 00 00; | goto #gsw03a_btn_common
0150 | 10 80 01 00 00 04 00 00; | load $bit=11
0151 | 22 FE 00 0D 04 00 00 00; | send.modbus $dev=fe $reg=13 $len=4
0152 | 04 01 00 00 00 00 00 00; | exit
0153 | 03 02 DF 01 00 00 00 00; | reuse #bath3_relax
0154 | 10 80 01 00 00 05 00 00; | load $hex=500
0155 | 22 FE 00 0D 04 00 00 00; | send.modbus $dev=fe $reg=13 $len=4
0156 | 01 01 00 00 DC 05 00 00; | wait $sec=0.15
0157 | 10 80 01 00 40 05 00 00; | load $hex=540
0158 | 22 FE 00 0D 04 00 00 00; | send.modbus $dev=fe $reg=13 $len=4
0159 | 03 02 50 01 F0 49 02 00; | reuse #gsw03b_refresh $sec=15
015A | 04 01 00 00 00 00 00 00; | exit
015B | 03 02 E2 01 00 00 00 00; | reuse #bath3_master
015C | 10 80 01 00 40 04 00 00; | load $hex=440
015D | 01 01 55 01 00 00 00 00; | goto #gsw03b_btn_common
015E | 03 02 E5 01 00 00 00 00; | reuse #bath3_night
015F | 10 80 01 00 40 01 00 00; | load $hex=140
0160 | 01 01 55 01 00 00 00 00; | goto #gsw03b_btn_common
0161 | 10 80 01 00 00 04 00 00; | load $bit=11
0162 | 22 FE 00 0D 04 00 00 00; | send.modbus $dev=fe $reg=13 $len=4
0163 | 04 01 00 00 00 00 00 00; | exit
0164 | 03 02 E8 01 00 00 00 00; | reuse #master_bath_relax
0165 | 10 80 01 00 00 05 00 00; | load $hex=500
0166 | 22 FE 00 0D 04 00 00 00; | send.modbus $dev=fe $reg=13 $len=4
0167 | 01 01 00 00 DC 05 00 00; | wait $sec=0.15
0168 | 10 80 01 00 40 05 00 00; | load $hex=540
0169 | 22 FE 00 0D 04 00 00 00; | send.modbus $dev=fe $reg=13 $len=4
016A | 03 02 61 01 F0 49 02 00; | reuse #gsw03c_refresh $sec=15
016B | 04 01 00 00 00 00 00 00; | exit
016C | 03 02 EB 01 00 00 00 00; | reuse #master_bath_master
016D | 10 80 01 00 40 04 00 00; | load $hex=440
016E | 01 01 66 01 00 00 00 00; | goto #gsw03c_btn_common
016F | 03 02 EE 01 00 00 00 00; | reuse #master_bath_night
0170 | 10 80 01 00 40 01 00 00; | load $hex=140
0171 | 01 01 66 01 00 00 00 00; | goto #gsw03c_btn_common
0172 | 10 80 01 00 00 00 00 00; | load $dec=0
0173 | 22 FE 00 0D 04 00 00 00; | send.modbus $dev=fe $reg=13 $len=4
0174 | 04 01 00 00 00 00 00 00; | exit
0175 | 03 02 BB 01 00 00 00 00; | reuse #bed2_relax
0176 | 10 80 01 00 00 04 00 00; | load $hex=400
0177 | 22 FE 00 0D 04 00 00 00; | send.modbus $dev=fe $reg=13 $len=4
0178 | 01 01 00 00 DC 05 00 00; | wait $sec=0.15
0179 | 10 80 01 00 40 04 00 00; | load $hex=440
017A | 22 FE 00 0D 04 00 00 00; | send.modbus $dev=fe $reg=13 $len=4
017B | 03 02 72 01 F0 49 02 00; | reuse #gsw02a_refresh $sec=15
017C | 04 01 00 00 00 00 00 00; | exit
017D | 03 02 C1 01 00 00 00 00; | reuse #bed2_light
017E | 10 80 01 00 40 00 00 00; | load $hex=40
017F | 01 01 77 01 00 00 00 00; | goto #gsw02a_btn_common
0180 | 10 80 01 00 00 00 00 00; | load $dec=0
0181 | 22 FE 00 0D 04 00 00 00; | send.modbus $dev=fe $reg=13 $len=4
0182 | 04 01 00 00 00 00 00 00; | exit
0183 | 03 02 C7 01 00 00 00 00; | reuse #bed3_relax
0184 | 10 80 01 00 00 04 00 00; | load $hex=400
0185 | 22 FE 00 0D 04 00 00 00; | send.modbus $dev=fe $reg=13 $len=4
0186 | 01 01 00 00 DC 05 00 00; | wait $sec=0.15
0187 | 10 80 01 00 40 04 00 00; | load $hex=440
0188 | 22 FE 00 0D 04 00 00 00; | send.modbus $dev=fe $reg=13 $len=4
0189 | 03 02 80 01 F0 49 02 00; | reuse #gsw02b_refresh $sec=15
018A | 04 01 00 00 00 00 00 00; | exit
018B | 03 02 CD 01 00 00 00 00; | reuse #bed3_light
018C | 10 80 01 00 40 00 00 00; | load $hex=40
018D | 01 01 85 01 00 00 00 00; | goto #gsw02b_btn_common
018E | 10 80 01 00 00 00 00 00; | load $dec=0
018F | 22 FE 00 0D 04 00 00 00; | send.modbus $dev=fe $reg=13 $len=4
0190 | 04 01 00 00 00 00 00 00; | exit
0191 | 03 02 D0 01 00 00 00 00; | reuse #master_bed_relax
0192 | 10 80 01 00 00 04 00 00; | load $hex=400
0193 | 22 FE 00 0D 04 00 00 00; | send.modbus $dev=fe $reg=13 $len=4
0194 | 01 01 00 00 DC 05 00 00; | wait $sec=0.15
0195 | 10 80 01 00 40 04 00 00; | load $hex=440
0196 | 22 FE 00 0D 04 00 00 00; | send.modbus $dev=fe $reg=13 $len=4
0197 | 03 02 8E 01 F0 49 02 00; | reuse #gsw02c_refresh $sec=15
0198 | 04 01 00 00 00 00 00 00; | exit
0199 | 03 02 D3 01 00 00 00 00; | reuse #master_bed_light
019A | 10 80 01 00 40 00 00 00; | load $hex=40
019B | 01 01 93 01 00 00 00 00; | goto #gsw02c_btn_common
019C | 10 80 01 00 00 00 00 00; | load $dec=0
019D | 22 FE 00 0D 04 00 00 00; | send.modbus $dev=fe $reg=13 $len=4
019E | 04 01 00 00 00 00 00 00; | exit
019F | 03 02 F1 01 00 00 00 00; | reuse #corridor_light
01A0 | 10 80 01 00 00 00 00 00; | load $hex=0
01A1 | 22 FE 00 0D 04 00 00 00; | send.modbus $dev=fe $reg=13 $len=4
01A2 | 01 01 00 00 DC 05 00 00; | wait $sec=0.15
01A3 | 10 80 01 00 00 01 00 00; | load $hex=100
01A4 | 22 FE 00 0D 04 00 00 00; | send.modbus $dev=fe $reg=13 $len=4
01A5 | 03 02 9C 01 F0 49 02 00; | reuse #gsw01_refresh $sec=15
01A6 | 04 01 00 00 00 00 00 00; | exit
01A7 | 10 80 0A 00 16 00 00 00; | load $var=workflow
01A8 | 10 81 12 00 01 00 00 00; | save modbus $var=m_workflow
01A9 | 04 01 00 00 00 00 00 00; | exit
01AA | 03 02 AC 01 10 27 00 00; | reuse #use_send_rcu_relays $sec=1
01AB | 04 01 00 00 00 00 00 00; | exit
01AC | 02 03 00 00 00 00 00 00; | rcu.read relays
01AD | 10 81 12 00 02 00 00 00; | save modbus $var=m_rcu_relays
01AE | 04 01 00 00 00 00 00 00; | exit
01AF | 10 80 01 00 01 00 00 00; | load $dec=1
01B0 | 10 81 12 00 03 00 00 00; | save modbus $var=m_bed1_panel
01B1 | 04 01 00 00 00 00 00 00; | exit
01B2 | 10 80 01 00 02 00 00 00; | load $dec=2
01B3 | 10 81 12 00 03 00 00 00; | save modbus $var=m_bed1_panel
01B4 | 04 01 00 00 00 00 00 00; | exit
01B5 | 10 80 01 00 03 00 00 00; | load $dec=3
01B6 | 10 81 12 00 03 00 00 00; | save modbus $var=m_bed1_panel
01B7 | 04 01 00 00 00 00 00 00; | exit
01B8 | 10 80 01 00 01 00 00 00; | load $dec=1
01B9 | 10 81 12 00 04 00 00 00; | save modbus $var=m_bed2_panel
01BA | 04 01 00 00 00 00 00 00; | exit
01BB | 10 80 01 00 02 00 00 00; | load $dec=2
01BC | 10 81 12 00 04 00 00 00; | save modbus $var=m_bed2_panel
01BD | 04 01 00 00 00 00 00 00; | exit
01BE | 10 80 01 00 03 00 00 00; | load $dec=3
01BF | 10 81 12 00 04 00 00 00; | save modbus $var=m_bed2_panel
01C0 | 04 01 00 00 00 00 00 00; | exit
01C1 | 10 80 01 00 04 00 00 00; | load $dec=4
01C2 | 10 81 12 00 04 00 00 00; | save modbus $var=m_bed2_panel
01C3 | 04 01 00 00 00 00 00 00; | exit
01C4 | 10 80 01 00 01 00 00 00; | load $dec=1
01C5 | 10 81 12 00 05 00 00 00; | save modbus $var=m_bed3_panel
01C6 | 04 01 00 00 00 00 00 00; | exit
01C7 | 10 80 01 00 02 00 00 00; | load $dec=2
01C8 | 10 81 12 00 05 00 00 00; | save modbus $var=m_bed3_panel
01C9 | 04 01 00 00 00 00 00 00; | exit
01CA | 10 80 01 00 03 00 00 00; | load $dec=3
01CB | 10 81 12 00 05 00 00 00; | save modbus $var=m_bed3_panel
01CC | 04 01 00 00 00 00 00 00; | exit
01CD | 10 80 01 00 04 00 00 00; | load $dec=4
01CE | 10 81 12 00 05 00 00 00; | save modbus $var=m_bed3_panel
01CF | 04 01 00 00 00 00 00 00; | exit
01D0 | 10 80 01 00 01 00 00 00; | load $dec=1
01D1 | 10 81 12 00 09 00 00 00; | save modbus $var=m_master_bed_panel
01D2 | 04 01 00 00 00 00 00 00; | exit
01D3 | 10 80 01 00 02 00 00 00; | load $dec=2
01D4 | 10 81 12 00 09 00 00 00; | save modbus $var=m_master_bed_panel
01D5 | 04 01 00 00 00 00 00 00; | exit
01D6 | 10 80 01 00 01 00 00 00; | load $dec=1
01D7 | 10 81 12 00 06 00 00 00; | save modbus $var=m_bath2_panel
01D8 | 04 01 00 00 00 00 00 00; | exit
01D9 | 10 80 01 00 02 00 00 00; | load $dec=2
01DA | 10 81 12 00 06 00 00 00; | save modbus $var=m_bath2_panel
01DB | 04 01 00 00 00 00 00 00; | exit
01DC | 10 80 01 00 03 00 00 00; | load $dec=3
01DD | 10 81 12 00 06 00 00 00; | save modbus $var=m_bath2_panel
01DE | 04 01 00 00 00 00 00 00; | exit
01DF | 10 80 01 00 01 00 00 00; | load $dec=1
01E0 | 10 81 12 00 07 00 00 00; | save modbus $var=m_bath3_panel
01E1 | 04 01 00 00 00 00 00 00; | exit
01E2 | 10 80 01 00 02 00 00 00; | load $dec=2
01E3 | 10 81 12 00 07 00 00 00; | save modbus $var=m_bath3_panel
01E4 | 04 01 00 00 00 00 00 00; | exit
01E5 | 10 80 01 00 03 00 00 00; | load $dec=3
01E6 | 10 81 12 00 07 00 00 00; | save modbus $var=m_bath3_panel
01E7 | 04 01 00 00 00 00 00 00; | exit
01E8 | 10 80 01 00 01 00 00 00; | load $dec=1
01E9 | 10 81 12 00 08 00 00 00; | save modbus $var=m_master_bath_panel
01EA | 04 01 00 00 00 00 00 00; | exit
01EB | 10 80 01 00 02 00 00 00; | load $dec=2
01EC | 10 81 12 00 08 00 00 00; | save modbus $var=m_master_bath_panel
01ED | 04 01 00 00 00 00 00 00; | exit
01EE | 10 80 01 00 03 00 00 00; | load $dec=3
01EF | 10 81 12 00 08 00 00 00; | save modbus $var=m_master_bath_panel
01F0 | 04 01 00 00 00 00 00 00; | exit
01F1 | 02 0B 01 00 08 00 00 00; | rcu.xor $relay=4
01F2 | 01 01 AA 01 00 00 00 00; | goto #send_rcu_relays
01F3 | 08 01 F7 01 00 00 00 00; | if equal #modbus_user_receive $dec=0
01F4 | 08 01 FA 01 01 00 00 00; | if equal #modbus_workflow_receive $dec=1
01F5 | 08 01 03 02 02 00 00 00; | if equal #receive_rcu_relays $dec=2
01F6 | 04 01 00 00 00 00 00 00; | exit
01F7 | 10 80 12 00 00 00 00 00; | load modbus $var=m_user
01F8 | 10 81 0A 00 15 00 00 00; | save $var=user
01F9 | 04 01 00 00 00 00 00 00; | exit
01FA | 10 80 12 00 01 00 00 00; | load modbus $var=m_workflow
01FB | 10 81 0A 00 16 00 00 00; | save $var=workflow
01FC | 03 02 25 00 00 00 00 00; | reuse #gsw04a_refresh
01FD | 03 02 54 00 00 00 00 00; | reuse #gsw04b_refresh
01FE | 03 02 83 00 00 00 00 00; | reuse #gsw04c_refresh
01FF | 03 02 B2 00 00 00 00 00; | reuse #gsw04d_refresh
0200 | 03 02 E1 00 00 00 00 00; | reuse #gsw04e_refresh
0201 | 03 02 10 01 00 00 00 00; | reuse #gsw04f_refresh
0202 | 04 01 00 00 00 00 00 00; | exit
0203 | 10 80 12 00 02 00 00 00; | load modbus $var=m_rcu_relays
0204 | 02 04 00 00 00 00 00 00; | rcu.set all relays from acc
0205 | 04 01 00 00 00 00 00 00; | exit

## Settings2
00 | 02; | 2 | MAC Address | 1 |  |  |  |  | Dir: | C:\tini\ModularHotel\ABSlink\RCUmanager\bin\Release
01 | 01; | 1 |  | 2 |  |  |  |  | Settings page: | 0x0007D000
02 | 36; | 54 |  | 3 |  | 19
03 | 7D; | 125 |  | 4 |  | 109
04 | 6D; | 109 |  | 5 |  | 125
05 | 14; | 19 |  | 6 |  | 54
06 | C0; | 192 | Device IP | 1
07 | A8; | 168 |  | 2
08 | 01; | 1 |  | 3
09 | E0; | 224 |  | 4
0A | FF; | 255 | Mask | 1
0B | FF; | 255 |  | 2
0C | FF; | 255 |  | 3
0D | 00; | 0 |  | 4
0E | 82; | 130 | Gateway | 1
0F | 0A; | 10 |  | 2
10 | 01; | 1 |  | 3
11 | 01; | 1 |  | 4
12 | 10; | 16 | Port | Hi | 4096
13 | 00; | 0 |  | Low
14 | 00; | 0 | Devices/EventMap | 1 |  | Device list followed by event map
15 | C0; | 192 |  | 2 |  | (align 4 byte var/dest)
16 | 07; | 7 |  | 3
17 | 00; | 0 |  | 4
18 | 00; | 0 | AutoStart/Program | 1 |  | Autostart followed by program
19 | 80; | 128 | 0=above 63 blocks 80=standard below 63 blocks | 2 |  | (align 4 byte var/dest)
1A | 07; | 7 |  | 3
1B | 00; | 0 |  | 4
1C | 14; | 20 | DeviceNum | 4 |  | Devices number
1D | 04; | 4 | AutostartNum | Space |  | Number of elements in autoexec
1E | 82; | 130 | TH Server | 1 |  | ModBus pseudoadd FF
1F | 0A; | 10 |  | 2
20 | 01; | 1 |  | 3
21 | DC; | 220 |  | 4
22 | E8; | 232 | Site code | 1
23 | 03; | 3 |  | 2
24 | 00; | 0 |  | 3
25 | 00; | 0 |  | 4
26 | 00; | 0 |  | 5
27 | 00; | 0 |  | 6
28 | 00; | 0 |  | 7
29 | 00; | 0 |  | 8
2A | 81; | 129 | Room number | 1
2B | 00; | 0 |  | 2
2C | 00; | 0 | Building/Extension | 1
2D | 00; | 0 |  | 2
2E | 10; | 16 | TH server port | 1
2F | 00; | 0 |  | 2
30 | 53; | 83 | COM1 | Type |  | Master 115k | Processes sheet
31 | 53; | 83 | COM2 | Type |  | Master 115k
32 | D0; | 83 | COM3 | Type |  | Master 9.6k
33 | 00; | 0 | RF | Type |  | Slave 9600
34 | 01; | 1 | TCP/IP | Type |  | Slave
35 | 14; | 20 | COMTimeout | Par secs |  | Max timeout on answer (in 128 1/10000 secs, 20 =1/4 secs)
36 | 20; | 32 | COM Delay 1 | Tick |  | Delay between packets
37 | 32; | 50 | COM Delay 1 | Tick |  | Delay between packets
38 | 20; | 32 | COM Delay 1 | Tick |  | Delay between packets
39 | 07; | 7 | RCU Relay mask |  |  | security block, filter out thermo relays
3A | 00; | 0 | Thermo1 | Device Num |  | TAG
3B | 00; | 0 | Thermo1 | Type |  | 0=Null, 1=TAG base rel 1/0
3C | 00; | 0 | Thermo1 | Control device |  | 0=RCU, #=device num |  |  |  | 3 | open
3D | 00; | 0 | Thermo1 | Hot relay |  | 0=Null, 1-31 = rel, 32-33 = 0-10V |  |  |  | 4 | close
3E | 00; | 0 | Thermo1 | Cold relay |  | 0=Null, 1-31 = rel, 32-33 = 0-10V
3F | 00; | 0 | Thermo1 | Speed1 relay |  | 0=Null, 1-31 = rel
40 | 00; | 0 | Thermo1 | Speed2 relay |  | 0=Null, 1-31 = rel |  |  |  | 10010011 | 93;
41 | 00; | 0 | Thermo1 | Speed3 relay |  | 0=Null, 1-31 = rel
42 | 00; | 0 | Thermo1 | Window contact |  | 87th bits 00Rcu/01Tag/10Dev, 20h=0NO 1NC, 00hNone, 0fh #Input
43 | 00; | 0 | Thermo2 | Device Num |  | TAG
44 | 00; | 0 | Thermo2 | Type |  | 0=Null, 1=TAG base rel 1/0
45 | 00; | 0 | Thermo2 | Control device |  | 0=RCU, #=device num
46 | 00; | 0 | Thermo2 | Hot relay |  | 0=Null, 1-31 = rel, 32-33 = 0-10V
47 | 00; | 0 | Thermo2 | Cold relay |  | 0=Null, 1-31 = rel, 32-33 = 0-10V
48 | 00; | 0 | Thermo2 | Speed1 relay |  | 0=Null, 1-31 = rel
49 | 00; | 0 | Thermo2 | Speed2 relay |  | 0=Null, 1-31 = rel
4A | 00; | 0 | Thermo2 | Speed3 relay |  | 0=Null, 1-31 = rel
4B | 00; | 0 | Thermo2 | Window contact |  | 87th bits 00Rcu/01Tag/10Dev, 00hNone, #Input number
4C | 00; | 0 | Thermo3 | Device Num |  | TAG
4D | 00; | 0 | Thermo3 | Type |  | 0=Null, 1=TAG base rel 1/0
4E | 00; | 0 | Thermo3 | Control device |  | 0=RCU, #=device num
4F | 00; | 0 | Thermo3 | Hot relay |  | 0=Null, 1-31 = rel, 32-33 = 0-10V
50 | 00; | 0 | Thermo3 | Cold relay |  | 0=Null, 1-31 = rel, 32-33 = 0-10V
51 | 00; | 0 | Thermo3 | Speed1 relay |  | 0=Null, 1-31 = rel
52 | 00; | 0 | Thermo3 | Speed2 relay |  | 0=Null, 1-31 = rel
53 | 00; | 0 | Thermo3 | Speed3 relay |  | 0=Null, 1-31 = rel
54 | 00; | 0 | Thermo3 | Window contact |  | 87th bits 00Rcu/01Tag/10Dev, 00hNone, #Input number
55 | 00; | 0 | Thermo4 | Device Num |  | TAG
56 | 00; | 0 | Thermo4 | Type |  | 0=Null, 1=TAG base rel 1/0
57 | 00; | 0 | Thermo4 | Control device |  | 0=RCU, #=device num
58 | 00; | 0 | Thermo4 | Hot relay |  | 0=Null, 1-31 = rel, 32-33 = 0-10V
59 | 00; | 0 | Thermo4 | Cold relay |  | 0=Null, 1-31 = rel, 32-33 = 0-10V
5A | 00; | 0 | Thermo4 | Speed1 relay |  | 0=Null, 1-31 = rel
5B | 00; | 0 | Thermo4 | Speed2 relay |  | 0=Null, 1-31 = rel
5C | 00; | 0 | Thermo4 | Speed3 relay |  | 0=Null, 1-31 = rel
5D | 00; | 0 | Thermo4 | Window contact |  | 87th bits 00Rcu/01Tag/10Dev, 00hNone, #Input number
5E | 00; | 0 | Thermo5 | Device Num |  | TAG
5F | 00; | 0 | Thermo5 | Type |  | 0=Null, 1=TAG base rel 1/0
60 | 00; | 0 | Thermo5 | Control device |  | 0=RCU, #=device num
61 | 00; | 0 | Thermo5 | Hot relay |  | 0=Null, 1-31 = rel, 32-33 = 0-10V
62 | 00; | 0 | Thermo5 | Cold relay |  | 0=Null, 1-31 = rel, 32-33 = 0-10V
63 | 00; | 0 | Thermo5 | Speed1 relay |  | 0=Null, 1-31 = rel
64 | 00; | 0 | Thermo5 | Speed2 relay |  | 0=Null, 1-31 = rel
65 | 00; | 0 | Thermo5 | Speed3 relay |  | 0=Null, 1-31 = rel
66 | 00; | 0 | Thermo5 | Window contact |  | 87th bits 00Rcu/01Tag/10Dev, 00hNone, #Input number
67 | 00; | 0 | Thermo6 | Device Num |  | TAG
68 | 00; | 0 | Thermo6 | Type |  | 0=Null, 1=TAG base rel 1/0
69 | 00; | 0 | Thermo6 | Control device |  | 0=RCU, #=device num
6A | 00; | 0 | Thermo6 | Hot relay |  | 0=Null, 1-31 = rel, 32-33 = 0-10V
6B | 00; | 0 | Thermo6 | Cold relay |  | 0=Null, 1-31 = rel, 32-33 = 0-10V
6C | 00; | 0 | Thermo6 | Speed1 relay |  | 0=Null, 1-31 = rel
6D | 00; | 0 | Thermo6 | Speed2 relay |  | 0=Null, 1-31 = rel
6E | 00; | 0 | Thermo6 | Speed3 relay |  | 0=Null, 1-31 = rel
6F | 00; | 0 | Thermo6 | Window contact |  | 8th bit 0Rcu/1Tag, 0None, #Input number
70 | 14; | 20 | Thermo* | Speed Ratio |  | FanSpeed=Temperature delta in decimals / ratio
71 | 05; | 5 | Thermo* | Valve Ratio |  | Valve 0-100%= delta temp in cent / ratio
72 | 00; | 0
73 | 00; | 0
74 | 00; | 0 | Thermo* | RunTime Cold | 1 | Running time for the valve in TICK
75 | 00; | 0 | Thermo* | RunTime Cold | 2 | es. 190 sec= 10000*190
76 | 00; | 0 | Thermo* | RunTime Cold | 3 |  | 0 | 00000000
77 | 00; | 0 | Thermo* | RunTime Cold | 4
78 | 00; | 0 | Thermo* | RunTime Hot | 1
79 | 00; | 0 | Thermo* | RunTime Hot | 2
7A | 00; | 0 | Thermo* | RunTime Hot | 3 |  | 0 | 00000000
7B | 00; | 0 | Thermo* | RunTime Hot | 4
7C | 00; | 0
7D | 00; | 0
7E | 00; | 0
7F | 01; | 1
80 | 10; | 16 | Roles opening door | low |  | Permit to define staff open the door
81 | 00; | 0 | Roles opening door | high
82 | 01; | 1 | Ablitate groups opening |  |  | bit1=true
83 | 18; | 24 | Roles blocked by | low |  | HK and HKS
84 | 00; | 0 | flag on event | high
85 | 00; | 0 | RfId mode |  |  | 0=standard, 1=Vingcard mixed
86 | 00; | 0 | RfId data |  |  | On Vingcard mode = starting info for staff
87 | 00; | 0
88 | 01; | 1 | Type of calculation for open valve |  |  | 0=standard, 1=japanese algorithm
89 | 00; | 0
8A | 01; | 1 | Battery if=1 from program, if=0 charging |  |  | bit 0=0 Output on, 1=0 if battery dor lock 100% to-do add new HW
8B | 00; | 0 | Delay on server error |  |  | amount of delay before next send, 0=1 second else (1/10000)<<val
8C | 00; | 0 | FAN remap on valve mode |  |  | 1= fan based on valves according the remap table below
8D | 00; | 0 | Fan1 Fan1 from valve %
8E | 00; | 0 | Fan2 Fan2 from valve %
8F | 00; | 0 | Fan3 Fan3 from valve %
90 | 03; | 3 | BSP1
91 | 00; | 0
92 | 01; | 1
93 | 80; | 128
94 | 00; | 0 | BSP2
95 | 00; | 0
96 | 00; | 0
97 | 00; | 0
98 | 00; | 0 | BSP3
99 | 00; | 0
9A | 00; | 0
9B | 00; | 0
9C | 00; | 0 | BSP4
9D | 00; | 0
9E | 00; | 0
9F | 00; | 0
A0 | 00; | 0 | BSP5
A1 | 00; | 0
A2 | 00; | 0
A3 | 00; | 0
A4 | 00; | 0 | BSP6
A5 | 00; | 0
A6 | 00; | 0
A7 | 00; | 0
A8 | 00; | 0
A9 | 00; | 0
AA | 00; | 0
AB | 00; | 0
AC | 00; | 0
AD | 00; | 0
AE | 00; | 0
AF | 00; | 0
B0 | 00; | 0
B1 | 00; | 0
B2 | 00; | 0
B3 | 00; | 0
B4 | 00; | 0
B5 | 00; | 0
B6 | 00; | 0
B7 | 00; | 0
B8 | 00; | 0
B9 | 00; | 0
BA | 00; | 0
BB | 00; | 0
BC | 00; | 0
BD | 00; | 0
BE | 00; | 0
BF | 00; | 0
C0 | 00; |  | COM4 BusExt |  | !=0 = Activate |  | 3D-5D Kaba - 50 WiFi -10.50.53 ZigBee master 50 vingcard;
C1 | 00; | 1 | COM Ext Type |  | 0, 1=Kaba, 2=WiFi/ZigBee transparent, 3=ZigBeeMaster, 4=WiFiMaster Digi API
C2 | 01; | 1 | Expansio bus type |  | 1=COM, 2=8 relays
C3 | 00; | 0 | Number of locks |  | Address specified on ZigBee addresses from 0x300
C4 | 00; | 0 | ZeroCrossing on Input 8 | 1 | Delay RelayOn/Off on zero crossing (1 activate, >1 delay in TICK)
C5 | 00; | 0 | ZeroCrossing on Input | 2
C6 | 00; | 0 | ZeroCrossing on Input | 3
C7 | 00; | 0 | ZeroCrossing on Input | 4
C8 | 00; | 0 | Offset GMT time -> UTC | 1 | Offset signed INT 32 bit
C9 | 00; | 0 | params set to AUS time | 2 |  | 0 | GMT
CA | 00; | 0 |  | 3 |  | 0 | val
CB | 00; | 0 |  | 4 |  |  | FFFFFFFF-hex(GMT *3600)
CC | 00; | 0
CD | 00; | 0
CE | 00; | 0
CF | 00; | 0
D0 | 00; | 0
D1 | 00; | 0
D2 | 00; | 0
D3 | 00; | 0
D4 | 00; | 0
D5 | 00; | 0
D6 | 00; | 0
D7 | 00; | 0
D8 | 00; | 0
D9 | 00; | 0
DA | 00; | 0
DB | 00; | 0
DC | 00; | 0
DD | 00; | 0
DE | 00; | 0
DF | 00; | 0
E0 | 00; | 0
E1 | 00; | 0
E2 | 00; | 0
E3 | 00; | 0
E4 | 00; | 0
E5 | 00; | 0
E6 | 00; | 0
E7 | 00; | 0
E8 | 00; | 0
E9 | 00; | 0
EA | 00; | 0
EB | 00; | 0
EC | 00; | 0
ED | 00; | 0
EE | 00; | 0
EF | 00; | 0
F0 | 00; | 0
F1 | 00; | 0
F2 | 00; | 0
F3 | 00; | 0
F4 | 00; | 0
F5 | 00; | 0
F6 | 00; | 0
F7 | 00; | 0
F8 | 00; | 0
F9 | 00; | 0
FA | 00; | 0
FB | 00; | 0
FC | 00; | 0
FD | 00; | 0
FE | 00; | 0
FF | 00; | 0
100 | 02; | 2 | Enabled groups |  | 0 |  | Group | 000-007
101 | 00; | 0 |  |  | 1 |  |  | 008-015
102 | 00; | 0 |  |  | 2 |  |  | 016-023
103 | 00; | 0 |  |  | 3
104 | 00; | 0 |  |  | 4
105 | 00; | 0 |  |  | 5
106 | 00; | 0 |  |  | 6
107 | 00; | 0 |  |  | 7
108 | 00; | 0 |  |  | 8
109 | 00; | 0 |  |  | 9
10A | 00; | 0 |  |  | 10
10B | 00; | 0 |  |  | 11
10C | 00; | 0 |  |  | 12
10D | 00; | 0 |  |  | 13
10E | 00; | 0 |  |  | 14
10F | 00; | 0 |  |  | 15
110 | 00; | 0 |  |  | 16
111 | 00; | 0 |  |  | 17
112 | 00; | 0 |  |  | 18
113 | 00; | 0 |  |  | 19
114 | 00; | 0 |  |  | 20
115 | 00; | 0 |  |  | 21
116 | 00; | 0 |  |  | 22
117 | 00; | 0 |  |  | 23
118 | 00; | 0 |  |  | 24
119 | 00; | 0 |  |  | 25
11A | 00; | 0 |  |  | 26
11B | 00; | 0 |  |  | 27
11C | 00; | 0 |  |  | 28
11D | 00; | 0 |  |  | 29
11E | 00; | 0 |  |  | 30
11F | 00; | 0 |  |  | 31 |  |  | 248-255
120 | 00; | 0
121 | 00; | 0
122 | 00; | 0
123 | 00; | 0
124 | 00; | 0
125 | 00; | 0
126 | 00; | 0
127 | 00; | 0
128 | 00; | 0
129 | 00; | 0
12A | 00; | 0
12B | 00; | 0
12C | 00; | 0
12D | 00; | 0
12E | 00; | 0
12F | 00; | 0
130 | 00; | 0
131 | 00; | 0
132 | 00; | 0
133 | 00; | 0
134 | 00; | 0
135 | 00; | 0
136 | 00; | 0
137 | 00; | 0
138 | 00; | 0
139 | 00; | 0
13A | 00; | 0
13B | 00; | 0
13C | 00; | 0
13D | 00; | 0
13E | 00; | 0 |  |  | 30
13F | 00; | 0 |  |  | 31 |  |  | 248-255
140 | 02; | 2 | Enabled groups IDPG2 |  | 0 |  | Group | 000-007
141 | 00; | 0 |  |  | 1 |  |  | 008-015
142 | 00; | 0 |  |  | 2 |  |  | 016-023
143 | 00; | 0 |  |  | 3
144 | 00; | 0 |  |  | 4
145 | 00; | 0 |  |  | 5
146 | 00; | 0 |  |  | 6
147 | 00; | 0 |  |  | 7
148 | 00; | 0 |  |  | 8
149 | 00; | 0 |  |  | 9
14A | 00; | 0 |  |  | 10
14B | 00; | 0 |  |  | 11
14C | 00; | 0 |  |  | 12
14D | 00; | 0 |  |  | 13
14E | 00; | 0 |  |  | 14
14F | 00; | 0 |  |  | 15
150 | 00; | 0 |  |  | 16
151 | 00; | 0 |  |  | 17
152 | 00; | 0 |  |  | 18
153 | 00; | 0 |  |  | 19
154 | 00; | 0 |  |  | 20
155 | 00; | 0 |  |  | 21
156 | 00; | 0 |  |  | 22
157 | 00; | 0 |  |  | 23
158 | 00; | 0 |  |  | 24
159 | 00; | 0 |  |  | 25
15A | 00; | 0 |  |  | 26
15B | 00; | 0 |  |  | 27
15C | 00; | 0 |  |  | 28
15D | 00; | 0 |  |  | 29
15E | 00; | 0 |  |  | 30
15F | 00; | 0 |  |  | 31 |  |  | 248-255
160 | 02; | 2 | Enabled groups IDPG3 |  | 0 |  | Group | 000-007
161 | 00; | 0 |  |  | 1 |  |  | 008-015
162 | 00; | 0 |  |  | 2 |  |  | 016-023
163 | 00; | 0 |  |  | 3
164 | 00; | 0 |  |  | 4
165 | 00; | 0 |  |  | 5
166 | 00; | 0 |  |  | 6
167 | 00; | 0 |  |  | 7
168 | 00; | 0 |  |  | 8
169 | 00; | 0 |  |  | 9
16A | 00; | 0 |  |  | 10
16B | 00; | 0 |  |  | 11
16C | 00; | 0 |  |  | 12
16D | 00; | 0 |  |  | 13
16E | 00; | 0 |  |  | 14
16F | 00; | 0 |  |  | 15
170 | 00; | 0 |  |  | 16
171 | 00; | 0 |  |  | 17
172 | 00; | 0 |  |  | 18
173 | 00; | 0 |  |  | 19
174 | 00; | 0 |  |  | 20
175 | 00; | 0 |  |  | 21
176 | 00; | 0 |  |  | 22
177 | 00; | 0 |  |  | 23
178 | 00; | 0 |  |  | 24
179 | 00; | 0 |  |  | 25
17A | 00; | 0 |  |  | 26
17B | 00; | 0 |  |  | 27
17C | 00; | 0 |  |  | 28
17D | 00; | 0 |  |  | 29
17E | 00; | 0 |  |  | 30
17F | 00; | 0 |  |  | 31 |  |  | 248-255
180 | 02; | 2 | Enabled groups IDPG4 |  | 0 |  | Group | 000-007
181 | 00; | 0 |  |  | 1 |  |  | 008-015
182 | 00; | 0 |  |  | 2 |  |  | 016-023
183 | 00; | 0 |  |  | 3
184 | 00; | 0 |  |  | 4
185 | 00; | 0 |  |  | 5
186 | 00; | 0 |  |  | 6
187 | 00; | 0 |  |  | 7
188 | 00; | 0 |  |  | 8
189 | 00; | 0 |  |  | 9
18A | 00; | 0 |  |  | 10
18B | 00; | 0 |  |  | 11
18C | 00; | 0 |  |  | 12
18D | 00; | 0 |  |  | 13
18E | 00; | 0 |  |  | 14
18F | 00; | 0 |  |  | 15
190 | 00; | 0 |  |  | 16
191 | 00; | 0 |  |  | 17
192 | 00; | 0 |  |  | 18
193 | 00; | 0 |  |  | 19
194 | 00; | 0 |  |  | 20
195 | 00; | 0 |  |  | 21
196 | 00; | 0 |  |  | 22
197 | 00; | 0 |  |  | 23
198 | 00; | 0 |  |  | 24
199 | 00; | 0 |  |  | 25
19A | 00; | 0 |  |  | 26
19B | 00; | 0 |  |  | 27
19C | 00; | 0 |  |  | 28
19D | 00; | 0 |  |  | 29
19E | 00; | 0 |  |  | 30
19F | 00; | 0 |  |  | 31 |  |  | 248-255
1A0 | 02; | 2 | Enabled groups IDPG5 |  | 0 |  | Group | 000-007
1A1 | 00; | 0 |  |  | 1 |  |  | 008-015
1A2 | 00; | 0 |  |  | 2 |  |  | 016-023
1A3 | 00; | 0 |  |  | 3
1A4 | 00; | 0 |  |  | 4
1A5 | 00; | 0 |  |  | 5
1A6 | 00; | 0 |  |  | 6
1A7 | 00; | 0 |  |  | 7
1A8 | 00; | 0 |  |  | 8
1A9 | 00; | 0 |  |  | 9
1AA | 00; | 0 |  |  | 10
1AB | 00; | 0 |  |  | 11
1AC | 00; | 0 |  |  | 12
1AD | 00; | 0 |  |  | 13
1AE | 00; | 0 |  |  | 14
1AF | 00; | 0 |  |  | 15
1B0 | 00; | 0 |  |  | 16
1B1 | 00; | 0 |  |  | 17
1B2 | 00; | 0 |  |  | 18
1B3 | 00; | 0 |  |  | 19
1B4 | 00; | 0 |  |  | 20
1B5 | 00; | 0 |  |  | 21
1B6 | 00; | 0 |  |  | 22
1B7 | 00; | 0 |  |  | 23
1B8 | 00; | 0 |  |  | 24
1B9 | 00; | 0 |  |  | 25
1BA | 00; | 0 |  |  | 26
1BB | 00; | 0 |  |  | 27
1BC | 00; | 0 |  |  | 28
1BD | 00; | 0 |  |  | 29
1BE | 00; | 0 |  |  | 30
1BF | 00; | 0 |  |  | 31 |  |  | 248-255
1C0 | 02; | 2 | Enabled groups IDPG6 |  | 0 |  | Group | 000-007
1C1 | 00; | 0 |  |  | 1 |  |  | 008-015
1C2 | 00; | 0 |  |  | 2 |  |  | 016-023
1C3 | 00; | 0 |  |  | 3
1C4 | 00; | 0 |  |  | 4
1C5 | 00; | 0 |  |  | 5
1C6 | 00; | 0 |  |  | 6
1C7 | 00; | 0 |  |  | 7
1C8 | 00; | 0 |  |  | 8
1C9 | 00; | 0 |  |  | 9
1CA | 00; | 0 |  |  | 10
1CB | 00; | 0 |  |  | 11
1CC | 00; | 0 |  |  | 12
1CD | 00; | 0 |  |  | 13
1CE | 00; | 0 |  |  | 14
1CF | 00; | 0 |  |  | 15
1D0 | 00; | 0 |  |  | 16
1D1 | 00; | 0 |  |  | 17
1D2 | 00; | 0 |  |  | 18
1D3 | 00; | 0 |  |  | 19
1D4 | 00; | 0 |  |  | 20
1D5 | 00; | 0 |  |  | 21
1D6 | 00; | 0 |  |  | 22
1D7 | 00; | 0 |  |  | 23
1D8 | 00; | 0 |  |  | 24
1D9 | 00; | 0 |  |  | 25
1DA | 00; | 0 |  |  | 26
1DB | 00; | 0 |  |  | 27
1DC | 00; | 0 |  |  | 28
1DD | 00; | 0 |  |  | 29
1DE | 00; | 0 |  |  | 30
1DF | 00; | 0 |  |  | 31 |  |  | 248-255
1E0 | 02; | 2 | Enabled groups IDPG7 |  | 0 |  | Group | 000-007
1E1 | 00; | 0 |  |  | 1 |  |  | 008-015
1E2 | 00; | 0 |  |  | 2 |  |  | 016-023
1E3 | 00; | 0 |  |  | 3
1E4 | 00; | 0 |  |  | 4
1E5 | 00; | 0 |  |  | 5
1E6 | 00; | 0 |  |  | 6
1E7 | 00; | 0 |  |  | 7
1E8 | 00; | 0 |  |  | 8
1E9 | 00; | 0 |  |  | 9
1EA | 00; | 0 |  |  | 10
1EB | 00; | 0 |  |  | 11
1EC | 00; | 0 |  |  | 12
1ED | 00; | 0 |  |  | 13
1EE | 00; | 0 |  |  | 14
1EF | 00; | 0 |  |  | 15
1F0 | 00; | 0 |  |  | 16
1F1 | 00; | 0 |  |  | 17
1F2 | 00; | 0 |  |  | 18
1F3 | 00; | 0 |  |  | 19
1F4 | 00; | 0 |  |  | 20
1F5 | 00; | 0 |  |  | 21
1F6 | 00; | 0 |  |  | 22
1F7 | 00; | 0 |  |  | 23
1F8 | 00; | 0 |  |  | 24
1F9 | 00; | 0 |  |  | 25
1FA | 00; | 0 |  |  | 26
1FB | 00; | 0 |  |  | 27
1FC | 00; | 0 |  |  | 28
1FD | 00; | 0 |  |  | 29
1FE | 00; | 0 |  |  | 30
1FF | 00; | 0 |  |  | 31 |  |  | 248-255
200 | 00; | 0
201 | 00; | 0
202 | 00; | 0
203 | 00; | 0
204 | 00; | 0
205 | 00; | 0
206 | 00; | 0
207 | 00; | 0
208 | 00; | 0
209 | 00; | 0
20A | 00; | 0
20B | 00; | 0
20C | 00; | 0
20D | 00; | 0
20E | 00; | 0
20F | 00; | 0
210 | 00; | 0
211 | 00; | 0
212 | 00; | 0
213 | 00; | 0
214 | 00; | 0
215 | 00; | 0
216 | 00; | 0
217 | 00; | 0
218 | 00; | 0
219 | 00; | 0
21A | 00; | 0
21B | 00; | 0
21C | 00; | 0
21D | 00; | 0
21E | 00; | 0
21F | 00; | 0
220 | 00; | 0
221 | 00; | 0
222 | 00; | 0
223 | 00; | 0
224 | 00; | 0
225 | 00; | 0
226 | 00; | 0
227 | 00; | 0
228 | 00; | 0
229 | 00; | 0
22A | 00; | 0
22B | 00; | 0
22C | 00; | 0
22D | 00; | 0
22E | 00; | 0
22F | 00; | 0
230 | 00; | 0
231 | 00; | 0
232 | 00; | 0
233 | 00; | 0
234 | 00; | 0
235 | 00; | 0
236 | 00; | 0
237 | 00; | 0
238 | 00; | 0
239 | 00; | 0
23A | 00; | 0
23B | 00; | 0
23C | 00; | 0
23D | 00; | 0
23E | 00; | 0
23F | 00; | 0
240 | 00; | 0
241 | 00; | 0
242 | 00; | 0
243 | 00; | 0
244 | 00; | 0
245 | 00; | 0
246 | 00; | 0
247 | 00; | 0
248 | 00; | 0
249 | 00; | 0
24A | 00; | 0
24B | 00; | 0
24C | 00; | 0
24D | 00; | 0
24E | 00; | 0
24F | 00; | 0
250 | 00; | 0
251 | 00; | 0
252 | 00; | 0
253 | 00; | 0
254 | 00; | 0
255 | 00; | 0
256 | 00; | 0
257 | 00; | 0
258 | 00; | 0
259 | 00; | 0
25A | 00; | 0
25B | 00; | 0
25C | 00; | 0
25D | 00; | 0
25E | 00; | 0
25F | 00; | 0
260 | 00; | 0
261 | 00; | 0
262 | 00; | 0
263 | 00; | 0
264 | 00; | 0
265 | 00; | 0
266 | 00; | 0
267 | 00; | 0
268 | 00; | 0
269 | 00; | 0
26A | 00; | 0
26B | 00; | 0
26C | 00; | 0
26D | 00; | 0
26E | 00; | 0
26F | 00; | 0
270 | 00; | 0
271 | 00; | 0
272 | 00; | 0
273 | 00; | 0
274 | 00; | 0
275 | 00; | 0
276 | 00; | 0
277 | 00; | 0
278 | 00; | 0
279 | 00; | 0
27A | 00; | 0
27B | 00; | 0
27C | 00; | 0
27D | 00; | 0
27E | 00; | 0
27F | 00; | 0
280 | 00; | 0
281 | 00; | 0
282 | 00; | 0
283 | 00; | 0
284 | 00; | 0
285 | 00; | 0
286 | 00; | 0
287 | 00; | 0
288 | 00; | 0
289 | 00; | 0
28A | 00; | 0
28B | 00; | 0
28C | 00; | 0
28D | 00; | 0
28E | 00; | 0
28F | 00; | 0
290 | 00; | 0
291 | 00; | 0
292 | 00; | 0
293 | 00; | 0
294 | 00; | 0
295 | 00; | 0
296 | 00; | 0
297 | 00; | 0
298 | 00; | 0
299 | 00; | 0
29A | 00; | 0
29B | 00; | 0
29C | 00; | 0
29D | 00; | 0
29E | 00; | 0
29F | 00; | 0
2A0 | 00; | 0
2A1 | 00; | 0
2A2 | 00; | 0
2A3 | 00; | 0
2A4 | 00; | 0
2A5 | 00; | 0
2A6 | 00; | 0
2A7 | 00; | 0
2A8 | 00; | 0
2A9 | 00; | 0
2AA | 00; | 0
2AB | 00; | 0
2AC | 00; | 0
2AD | 00; | 0
2AE | 00; | 0
2AF | 00; | 0
2B0 | 00; | 0
2B1 | 00; | 0
2B2 | 00; | 0
2B3 | 00; | 0
2B4 | 00; | 0
2B5 | 00; | 0
2B6 | 00; | 0
2B7 | 00; | 0
2B8 | 00; | 0
2B9 | 00; | 0
2BA | 00; | 0
2BB | 00; | 0
2BC | 00; | 0
2BD | 00; | 0
2BE | 00; | 0
2BF | 00; | 0
2C0 | 00; | 0
2C1 | 00; | 0
2C2 | 00; | 0
2C3 | 00; | 0
2C4 | 00; | 0
2C5 | 00; | 0
2C6 | 00; | 0
2C7 | 00; | 0
2C8 | 00; | 0
2C9 | 00; | 0
2CA | 00; | 0
2CB | 00; | 0
2CC | 00; | 0
2CD | 00; | 0
2CE | 00; | 0
2CF | 00; | 0
2D0 | 00; | 0
2D1 | 00; | 0
2D2 | 00; | 0
2D3 | 00; | 0
2D4 | 00; | 0
2D5 | 00; | 0
2D6 | 00; | 0
2D7 | 00; | 0
2D8 | 00; | 0
2D9 | 00; | 0
2DA | 00; | 0
2DB | 00; | 0
2DC | 00; | 0
2DD | 00; | 0
2DE | 00; | 0
2DF | 00; | 0
2E0 | 00; | 0
2E1 | 00; | 0
2E2 | 00; | 0
2E3 | 00; | 0
2E4 | 00; | 0
2E5 | 00; | 0
2E6 | 00; | 0
2E7 | 00; | 0
2E8 | 00; | 0
2E9 | 00; | 0
2EA | 00; | 0
2EB | 00; | 0
2EC | 00; | 0
2ED | 00; | 0
2EE | 00; | 0
2EF | 00; | 0
2F0 | 00; | 0
2F1 | 00; | 0
2F2 | 00; | 0
2F3 | 00; | 0
2F4 | 00; | 0
2F5 | 00; | 0
2F6 | 00; | 0
2F7 | 00; | 0
2F8 | 00; | 0
2F9 | 00; | 0
2FA | 00; | 0
2FB | 00; | 0
2FC | 00; | 0
2FD | 00; | 0
2FE | 00; | 0
2FF | 00; | 0
300 | 00; | 0
301 | 00; | 0
302 | 00; | 0
303 | 00; | 0
304 | 00; | 0
305 | 00; | 0
306 | 00; | 0
307 | 00; | 0
308 | 00; | 0
309 | 00; | 0
30A | 00; | 0
30B | 00; | 0
30C | 00; | 0
30D | 00; | 0
30E | 00; | 0
30F | 00; | 0
310 | 00; | 0
311 | 00; | 0
312 | 00; | 0
313 | 00; | 0
314 | 00; | 0
315 | 00; | 0
316 | 00; | 0
317 | 00; | 0
318 | 00; | 0
319 | 00; | 0
31A | 00; | 0
31B | 00; | 0
31C | 00; | 0
31D | 00; | 0
31E | 00; | 0
31F | 00; | 0
320 | 00; | 0
321 | 00; | 0
322 | 00; | 0
323 | 00; | 0
324 | 00; | 0
325 | 00; | 0
326 | 00; | 0
327 | 00; | 0
328 | 00; | 0
329 | 00; | 0
32A | 00; | 0
32B | 00; | 0
32C | 00; | 0
32D | 00; | 0
32E | 00; | 0
32F | 00; | 0
330 | 00; | 0
331 | 00; | 0
332 | 00; | 0
333 | 00; | 0
334 | 00; | 0
335 | 00; | 0
336 | 00; | 0
337 | 00; | 0
338 | 00; | 0
339 | 00; | 0
33A | 00; | 0
33B | 00; | 0
33C | 00; | 0
33D | 00; | 0
33E | 00; | 0
33F | 00; | 0
340 | 00; | 0
341 | 00; | 0
342 | 00; | 0
343 | 00; | 0
344 | 00; | 0
345 | 00; | 0
346 | 00; | 0
347 | 00; | 0
348 | 00; | 0
349 | 00; | 0
34A | 00; | 0
34B | 00; | 0
34C | 00; | 0
34D | 00; | 0
34E | 00; | 0
34F | 00; | 0
350 | 00; | 0
351 | 00; | 0
352 | 00; | 0
353 | 00; | 0
354 | 00; | 0
355 | 00; | 0
356 | 00; | 0
357 | 00; | 0
358 | 00; | 0
359 | 00; | 0
35A | 00; | 0
35B | 00; | 0
35C | 00; | 0
35D | 00; | 0
35E | 00; | 0
35F | 00; | 0
360 | 00; | 0
361 | 00; | 0
362 | 00; | 0
363 | 00; | 0
364 | 00; | 0
365 | 00; | 0
366 | 00; | 0
367 | 00; | 0
368 | 00; | 0
369 | 00; | 0
36A | 00; | 0
36B | 00; | 0
36C | 00; | 0
36D | 00; | 0
36E | 00; | 0
36F | 00; | 0
370 | 00; | 0
371 | 00; | 0
372 | 00; | 0
373 | 00; | 0
374 | 00; | 0
375 | 00; | 0
376 | 00; | 0
377 | 00; | 0
378 | 00; | 0
379 | 00; | 0
37A | 00; | 0
37B | 00; | 0
37C | 00; | 0
37D | 00; | 0
37E | 00; | 0
37F | 00; | 0
380 | 00; | 0
381 | 00; | 0
382 | 00; | 0
383 | 00; | 0
384 | 00; | 0
385 | 00; | 0
386 | 00; | 0
387 | 00; | 0
388 | 00; | 0
389 | 00; | 0
38A | 00; | 0
38B | 00; | 0
38C | 00; | 0
38D | 00; | 0
38E | 00; | 0
38F | 00; | 0
390 | 00; | 0
391 | 00; | 0
392 | 00; | 0
393 | 00; | 0
394 | 00; | 0
395 | 00; | 0
396 | 00; | 0
397 | 00; | 0
398 | 00; | 0
399 | 00; | 0
39A | 00; | 0
39B | 00; | 0
39C | 00; | 0
39D | 00; | 0
39E | 00; | 0
39F | 00; | 0
3A0 | 00; | 0
3A1 | 00; | 0
3A2 | 00; | 0
3A3 | 00; | 0
3A4 | 00; | 0
3A5 | 00; | 0
3A6 | 00; | 0
3A7 | 00; | 0
3A8 | 00; | 0
3A9 | 00; | 0
3AA | 00; | 0
3AB | 00; | 0
3AC | 00; | 0
3AD | 00; | 0
3AE | 00; | 0
3AF | 00; | 0
3B0 | 00; | 0
3B1 | 00; | 0
3B2 | 00; | 0
3B3 | 00; | 0
3B4 | 00; | 0
3B5 | 00; | 0
3B6 | 00; | 0
3B7 | 00; | 0
3B8 | 00; | 0
3B9 | 00; | 0
3BA | 00; | 0
3BB | 00; | 0
3BC | 00; | 0
3BD | 00; | 0
3BE | 00; | 0
3BF | 00; | 0
3C0 | 00; | 0
3C1 | 00; | 0
3C2 | 00; | 0
3C3 | 00; | 0
3C4 | 00; | 0
3C5 | 00; | 0
3C6 | 00; | 0
3C7 | 00; | 0
3C8 | 00; | 0
3C9 | 00; | 0
3CA | 00; | 0
3CB | 00; | 0
3CC | 00; | 0
3CD | 00; | 0
3CE | 00; | 0
3CF | 00; | 0
3D0 | 00; | 0
3D1 | 00; | 0
3D2 | 00; | 0
3D3 | 00; | 0
3D4 | 00; | 0
3D5 | 00; | 0
3D6 | 00; | 0
3D7 | 00; | 0
3D8 | 00; | 0
3D9 | 00; | 0
3DA | 00; | 0
3DB | 00; | 0
3DC | 00; | 0
3DD | 00; | 0
3DE | 00; | 0
3DF | 00; | 0
3E0 | 00; | 0
3E1 | 00; | 0
3E2 | 00; | 0
3E3 | 00; | 0
3E4 | 00; | 0
3E5 | 00; | 0
3E6 | 00; | 0
3E7 | 00; | 0
3E8 | 00; | 0
3E9 | 00; | 0
3EA | 00; | 0
3EB | 00; | 0
3EC | 00; | 0
3ED | 00; | 0
3EE | 00; | 0
3EF | 00; | 0
3F0 | 00; | 0
3F1 | 00; | 0
3F2 | 00; | 0
3F3 | 00; | 0
3F4 | 00; | 0
3F5 | 00; | 0
3F6 | 00; | 0
3F7 | 00; | 0
3F8 | 00; | 0
3F9 | 00; | 0
3FA | 00; | 0
3FB | 00; | 0
3FC | 00; | 0
3FD | 00; | 0
3FE | 00; | 0
3FF | 00; | 0
400 | 00; | 0
401 | 00; | 0
402 | 00; | 0
403 | 00; | 0
404 | 00; | 0
405 | 00; | 0
406 | 00; | 0
407 | 00; | 0
408 | 00; | 0
409 | 00; | 0
40A | 00; | 0
40B | 00; | 0
40C | 00; | 0
40D | 00; | 0
40E | 00; | 0
40F | 00; | 0
410 | 00; | 0
411 | 00; | 0
412 | 00; | 0
413 | 00; | 0
414 | 00; | 0
415 | 00; | 0
416 | 00; | 0
417 | 00; | 0
418 | 00; | 0
419 | 00; | 0
41A | 00; | 0
41B | 00; | 0
41C | 00; | 0
41D | 00; | 0
41E | 00; | 0
41F | 00; | 0
420 | 00; | 0

## CustomVar2
Variable short name | Description for variable
80 | last_action
82 | pir
85 | user_backup
86 | C/F

## ModbusVar2
Variable short name | Description for variable
0 | m_user
1 | m_workflow
2 | m_rcu_relays
3 | m_bed1_panel
4 | m_bed2_panel
5 | m_bed3_panel
6 | m_bath2_panel
7 | m_bath3_panel
8 | m_master_bath_panel
9 | m_master_bed_panel
A | m_notify | 0=restart 1=panelpress

## Device3
| ;Devices.hex | [9 empty] | Event map |  |  | Dir: | C:\tini\ModularHotel\ABSlink\RCUmanager\bin\Release
| ;Enum | Type | Id | COM | Pt Event map |  |  |  | lo hi |  | 16bit pt to program |  |  | 0000=none |  |  |  | Enum/Priority
| ;/Priority |  |  |  | lo hi |  | EnumHex | Enum | Progran |  | Start with RCU event |  |  | 8000=activate standard management |  |  |  | Enum is used in multi devices to manage variable offseting
1 | 00 | 00 | 00 | 00 | 00 00 | ; | 00 | 0 | 00 00; | RCU | Startup |  |  | 4000=only on guest presence
2 | 00 | 00 | 00 | 00 | 00 00 | ; | 01 | 1 | 00 00; |  | Watchdog |  |  | bit 15 permit to flag both (standard+program)
3 | 00 | 00 | 00 | 00 | 00 00 | ; | 02 | 2 | 00 00; |  | Battery | start |  | bit 14 only guest action
4 | 01 | 06 | 28 | 01 | 21 00 | ;GSW08 (entrance) | 03 | 3 | 00 00; |  | Battery | end
5 | 11 | 06 | 2E | 02 | 3C 00 | ;GSW05 A (master) | 04 | 4 | 00 00; |  | Battery | low |  | Types
6 | 21 | 06 | 2F | 02 | 57 00 | ;GSW05 B (master) | 05 | 5 | 00 00; |  | Input | 1 on |  | 1 | IDPG
7 | 31 | 06 | 2B | 01 | 72 00 | ;GSW04 (corridor) | 06 | 6 | 00 00; |  | Input | 1 off |  | 2 | TIG
8 | 41 | 06 | 2A | 01 | 8D 00 | ;GSW03 (bathroom) | 07 | 7 | 00 00; |  | Input | 2 on |  | 3 | TAG
9 | 51 | 06 | 29 | 01 | A8 00 | ;GSW02 (bed entry) | 08 | 8 | 00 00; |  | Input | 2 off |  | 4 | IOEXP
10 | 00 | 00 | 00 | 00 | 00 00 | ; | 09 | 9 | 00 00; |  | Input | 3 on |  | 5 | IODEXP
11 | 00 | 00 | 00 | 00 | 00 00 | ; | 0A | 10 | 00 00; |  | Input | 3 off |  | 6 | GSW |  | IOEXP with polling on Input
12 | 00 | 00 | 00 | 00 | 00 00 | ; | 0B | 11 | 00 00; |  | Input | 4 on |  | 7 | IOEXPIN
13 | 00 | 00 | 00 | 00 | 00 00 | ; | 0C | 12 | 00 00; |  | Input | 4 off |  | 8 | BSP RF
14 | 00 | 00 | 00 | 00 | 00 00 | ; | 0D | 13 | 00 00; |  | Input | 5 on |  | 9 | BSP wired
15 | 00 | 00 | 00 | 00 | 00 00 | ; | 0E | 14 | 00 00; |  | Input | 5 off |  | 128 | General Modbus
16 | 00 | 00 | 00 | 00 | 00 00 | ; | 0F | 15 | 00 00; |  | Input | 6 on |  | 129 | General IP |  | Id+Com=Port Pt=last 2 IP addr
17 | 00 | 00 | 00 | 00 | 00 00 | ; | 10 | 16 | 00 00; |  | Input | 6 off
18 | 00 | 00 | 00 | 00 | 00 00 | ; | 11 | 17 | 00 00; |  | Input | 7 on |  | Id | FF | Server
19 | 00 | 00 | 00 | 00 | 00 00 | ; | 12 | 18 | 00 00; |  | Input | 7 off |  |  | FE | Calling device
20 | 00 | 00 | 00 | 00 | 00 00 | ; | 13 | 19 | 00 00; |  | Input | 8 on
[7 empty] | 14 | 20 | 00 00; |  | Input | 8 off
[7 empty] | 15 | 21 | 00 00; |  | Thermo | on
[7 empty] | 16 | 22 | 5A 01; |  | Evt grp write (reg) |  | modbus_manager
[7 empty] | 17 | 23 | 00 00; |  | Evt grp write (reg)
[7 empty] | 18 | 24 | 00 00; |  | MUR | off
[7 empty] | 19 | 25 | 00 00; |  | SOS | on
[7 empty] | 1A | 26 | 00 00; |  | SOS | off
[7 empty] | 1B | 27 | 00 00; |  | Laundry | on
[7 empty] | 1C | 28 | 00 00; |  | Laundry | off
[7 empty] | 1D | 29 | 00 00; |  | Call | on
[7 empty] | 1E | 30 | 00 00; |  | Call | off
[7 empty] | 1F | 31 | 00 00; |  | Card Ok
[7 empty] | 20 | 32 | 00 00; |  | Card Nok
[7 empty] | 21 | 33 | 00 00; | GSW08 | OffLine
[7 empty] | 22 | 34 | 36 00; |  | Button | 1 on | gsw08_btn_1_dnd
[7 empty] | 23 | 35 | 00 00; |  | Button | 1 off
[7 empty] | 24 | 36 | 48 00; |  | Button | 2 on | gsw08_btn_2
[7 empty] | 25 | 37 | 00 00; |  | Button | 2 off
[7 empty] | 26 | 38 | 51 00; |  | Button | 3 on | gsw08_btn_3_mur
[7 empty] | 27 | 39 | 00 00; |  | Button | 3 off
[7 empty] | 28 | 40 | 63 00; |  | Button | 4 on | gsw08_btn_4
[7 empty] | 29 | 41 | 00 00; |  | Button | 4 off
[7 empty] | 2A | 42 | 00 00; |  | Button | 5 on
[7 empty] | 2B | 43 | 00 00; |  | Button | 5 off
[7 empty] | 2C | 44 | 67 00; |  | Button | 6 on | gsw08_btn_6
[7 empty] | 2D | 45 | 00 00; |  | Button | 6 off
[7 empty] | 2E | 46 | 00 00; |  | Button | 7 on
[7 empty] | 2F | 47 | 00 00; |  | Button | 7 off
[7 empty] | 30 | 48 | 00 00; |  | Button | 8 on
[7 empty] | 31 | 49 | 00 00; |  | Button | 8 off
[7 empty] | 32 | 50 | 00 00; |  | Button | 9 on
[7 empty] | 33 | 51 | 00 00; |  | Button | 9 off
[7 empty] | 34 | 52 | 6B 00; |  | Button | 10 on | gsw08_btn_10
[7 empty] | 35 | 53 | 00 00; |  | Button | 10 off
[7 empty] | 36 | 54 | 6F 00; |  | Button | 11 on | gsw08_btn_11
[7 empty] | 37 | 55 | 00 00; |  | Button | 11 off
[7 empty] | 38 | 56 | 73 00; |  | Button | 12 on | gsw08_btn_12
[7 empty] | 39 | 57 | 00 00; |  | Button | 12 off
[7 empty] | 3A | 58 | 0A 01; |  | motion | 13 on | pir1_close
[7 empty] | 3B | 59 | 00 00; |  | motion | 13 off
[7 empty] | 3C | 60 | 00 00; | GSW05 A | OffLine
[7 empty] | 3D | 61 | 00 00; |  | Button | 1 on
[7 empty] | 3E | 62 | 00 00; |  | Button | 1 off
[7 empty] | 3F | 63 | 00 00; |  | Button | 2 on
[7 empty] | 40 | 64 | 00 00; |  | Button | 2 off
[7 empty] | 41 | 65 | 00 00; |  | Button | 3 on
[7 empty] | 42 | 66 | 00 00; |  | Button | 3 off
[7 empty] | 43 | 67 | 80 00; |  | Button | 4 on | gsw05a_btn_4_dnd
[7 empty] | 44 | 68 | 00 00; |  | Button | 4 off
[7 empty] | 45 | 69 | 92 00; |  | Button | 5 on | gsw05a_btn_5
[7 empty] | 46 | 70 | 00 00; |  | Button | 5 off
[7 empty] | 47 | 71 | 9B 00; |  | Button | 6 on | gsw05a_btn_6
[7 empty] | 48 | 72 | 00 00; |  | Button | 6 off
[7 empty] | 49 | 73 | 9F 00; |  | Button | 7 on | gsw05a_btn_7
[7 empty] | 4A | 74 | 00 00; |  | Button | 7 off
[7 empty] | 4B | 75 | 00 00; |  | Button | 8 on
[7 empty] | 4C | 76 | 00 00; |  | Button | 8 off
[7 empty] | 4D | 77 | A3 00; |  | Button | 9 on | gsw05a_btn_9
[7 empty] | 4E | 78 | 00 00; |  | Button | 9 off
[7 empty] | 4F | 79 | 00 00; |  | Button | 10 on
[7 empty] | 50 | 80 | 00 00; |  | Button | 10 off
[7 empty] | 51 | 81 | 00 00; |  | Button | 11 on
[7 empty] | 52 | 82 | 00 00; |  | Button | 11 off
[7 empty] | 53 | 83 | 00 00; |  | Button | 12 on
[7 empty] | 54 | 84 | 00 00; |  | Button | 12 off
[7 empty] | 55 | 85 | 00 00; |  | motion | 13 on
[7 empty] | 56 | 86 | 00 00; |  | motion | 13 off
[7 empty] | 57 | 87 | 00 00; | GSW05 B | OffLine
[7 empty] | 58 | 88 | 00 00; |  | Button | 1 on
[7 empty] | 59 | 89 | 00 00; |  | Button | 1 off
[7 empty] | 5A | 90 | 00 00; |  | Button | 2 on
[7 empty] | 5B | 91 | 00 00; |  | Button | 2 off
[7 empty] | 5C | 92 | 00 00; |  | Button | 3 on
[7 empty] | 5D | 93 | 00 00; |  | Button | 3 off
[7 empty] | 5E | 94 | B0 00; |  | Button | 4 on | gsw05b_btn_4_dnd
[7 empty] | 5F | 95 | 00 00; |  | Button | 4 off
[7 empty] | 60 | 96 | C2 00; |  | Button | 5 on | gsw05b_btn_5
[7 empty] | 61 | 97 | 00 00; |  | Button | 5 off
[7 empty] | 62 | 98 | CB 00; |  | Button | 6 on | gsw05b_btn_6
[7 empty] | 63 | 99 | 00 00; |  | Button | 6 off
[7 empty] | 64 | 100 | CF 00; |  | Button | 7 on | gsw05b_btn_7
[7 empty] | 65 | 101 | 00 00; |  | Button | 7 off
[7 empty] | 66 | 102 | 00 00; |  | Button | 8 on
[7 empty] | 67 | 103 | 00 00; |  | Button | 8 off
[7 empty] | 68 | 104 | D3 00; |  | Button | 9 on | gsw05b_btn_9
[7 empty] | 69 | 105 | 00 00; |  | Button | 9 off
[7 empty] | 6A | 106 | 00 00; |  | Button | 10 on
[7 empty] | 6B | 107 | 00 00; |  | Button | 10 off
[7 empty] | 6C | 108 | 00 00; |  | Button | 11 on
[7 empty] | 6D | 109 | 00 00; |  | Button | 11 off
[7 empty] | 6E | 110 | 00 00; |  | Button | 12 on
[7 empty] | 6F | 111 | 00 00; |  | Button | 12 off
[7 empty] | 70 | 112 | 00 00; |  | motion | 13 on
[7 empty] | 71 | 113 | 00 00; |  | motion | 13 off
[7 empty] | 72 | 114 | 00 00; | GSW04 | OffLine
[7 empty] | 73 | 115 | 00 00; |  | Button | 1 on
[7 empty] | 74 | 116 | 00 00; |  | Button | 1 off
[7 empty] | 75 | 117 | 00 00; |  | Button | 2 on
[7 empty] | 76 | 118 | 00 00; |  | Button | 2 off
[7 empty] | 77 | 119 | 00 00; |  | Button | 3 on
[7 empty] | 78 | 120 | 00 00; |  | Button | 3 off
[7 empty] | 79 | 121 | DA 00; |  | Button | 4 on | gsw04_btn_4
[7 empty] | 7A | 122 | 00 00; |  | Button | 4 off
[7 empty] | 7B | 123 | 00 00; |  | Button | 5 on
[7 empty] | 7C | 124 | 00 00; |  | Button | 5 off
[7 empty] | 7D | 125 | E2 00; |  | Button | 6 on | gsw04_btn_6
[7 empty] | 7E | 126 | 00 00; |  | Button | 6 off
[7 empty] | 7F | 127 | E5 00; |  | Button | 7 on | gsw04_btn_7
[7 empty] | 80 | 128 | 00 00; |  | Button | 7 off
[7 empty] | 81 | 129 | 00 00; |  | Button | 8 on
[7 empty] | 82 | 130 | 00 00; |  | Button | 8 off
[7 empty] | 83 | 131 | E8 00; |  | Button | 9 on | gsw04_btn_9
[7 empty] | 84 | 132 | 00 00; |  | Button | 9 off
[7 empty] | 85 | 133 | 00 00; |  | Button | 10 on
[7 empty] | 86 | 134 | 00 00; |  | Button | 10 off
[7 empty] | 87 | 135 | 00 00; |  | Button | 11 on
[7 empty] | 88 | 136 | 00 00; |  | Button | 11 off
[7 empty] | 89 | 137 | 00 00; |  | Button | 12 on
[7 empty] | 8A | 138 | 00 00; |  | Button | 12 off
[7 empty] | 8B | 139 | 00 00; |  | motion | 13 on
[7 empty] | 8C | 140 | 00 00; |  | motion | 13 off
[7 empty] | 8D | 141 | 00 00; | GSW03 | OffLine
[7 empty] | 8E | 142 | 00 00; |  | Button | 1 on
[7 empty] | 8F | 143 | 00 00; |  | Button | 1 off
[7 empty] | 90 | 144 | 00 00; |  | Button | 2 on
[7 empty] | 91 | 145 | 00 00; |  | Button | 2 off
[7 empty] | 92 | 146 | 00 00; |  | Button | 3 on
[7 empty] | 93 | 147 | 00 00; |  | Button | 3 off
[7 empty] | 94 | 148 | EE 00; |  | Button | 4 on | gsw03_btn_4
[7 empty] | 95 | 149 | 00 00; |  | Button | 4 off
[7 empty] | 96 | 150 | F6 00; |  | Button | 5 on | gsw03_btn_5
[7 empty] | 97 | 151 | 00 00; |  | Button | 5 off
[7 empty] | 98 | 152 | F9 00; |  | Button | 6 on | gsw03_btn_6
[7 empty] | 99 | 153 | 00 00; |  | Button | 6 off
[7 empty] | 9A | 154 | 00 00; |  | Button | 7 on
[7 empty] | 9B | 155 | 00 00; |  | Button | 7 off
[7 empty] | 9C | 156 | 00 00; |  | Button | 8 on
[7 empty] | 9D | 157 | 00 00; |  | Button | 8 off
[7 empty] | 9E | 158 | 00 00; |  | Button | 9 on
[7 empty] | 9F | 159 | 00 00; |  | Button | 9 off
[7 empty] | A0 | 160 | 00 00; |  | Button | 10 on
[7 empty] | A1 | 161 | 00 00; |  | Button | 10 off
[7 empty] | A2 | 162 | 00 00; |  | Button | 11 on
[7 empty] | A3 | 163 | 00 00; |  | Button | 11 off
[7 empty] | A4 | 164 | 00 00; |  | Button | 12 on
[7 empty] | A5 | 165 | 00 00; |  | Button | 12 off
[7 empty] | A6 | 166 | 00 00; |  | motion | 13 on
[7 empty] | A7 | 167 | 00 00; |  | motion | 13 off
[7 empty] | A8 | 168 | 00 00; | GSW02 | OffLine
[7 empty] | A9 | 169 | 00 00; |  | Button | 1 on
[7 empty] | AA | 170 | 00 00; |  | Button | 1 off
[7 empty] | AB | 171 | 00 00; |  | Button | 2 on
[7 empty] | AC | 172 | 00 00; |  | Button | 2 off
[7 empty] | AD | 173 | 00 00; |  | Button | 3 on
[7 empty] | AE | 174 | 00 00; |  | Button | 3 off
[7 empty] | AF | 175 | FF 00; |  | Button | 4 on | gsw02_btn_4
[7 empty] | B0 | 176 | 00 00; |  | Button | 4 off
[7 empty] | B1 | 177 | 00 00; |  | Button | 5 on
[7 empty] | B2 | 178 | 00 00; |  | Button | 5 off
[7 empty] | B3 | 179 | 07 01; |  | Button | 6 on | gsw02_btn_6
[7 empty] | B4 | 180 | 00 00; |  | Button | 6 off
[7 empty] | B5 | 181 | 00 00; |  | Button | 7 on
[7 empty] | B6 | 182 | 00 00; |  | Button | 7 off
[7 empty] | B7 | 183 | 00 00; |  | Button | 8 on
[7 empty] | B8 | 184 | 00 00; |  | Button | 8 off
[7 empty] | B9 | 185 | 00 00; |  | Button | 9 on
[7 empty] | BA | 186 | 00 00; |  | Button | 9 off
[7 empty] | BB | 187 | 00 00; |  | Button | 10 on
[7 empty] | BC | 188 | 00 00; |  | Button | 10 off
[7 empty] | BD | 189 | 00 00; |  | Button | 11 on
[7 empty] | BE | 190 | 00 00; |  | Button | 11 off
[7 empty] | BF | 191 | 00 00; |  | Button | 12 on
[7 empty] | C0 | 192 | 00 00; |  | Button | 12 off
[7 empty] | C1 | 193 | 00 00; |  | motion | 13 on
[7 empty] | C2 | 194 | 00 00; |  | motion | 13 off

## XCODE3
XCODE [0.9,2]
0 | #startup
1 | version [35561452341814213551145390817034,9]
2 | goto #debugging
3 | reserved for ipad
4 | reserved for ipad
5 | reserved for ipad
6 | reserved for ipad
7 | reserved for ipad
8 | reserved for ipad
9 | reserved for ipad
10 | reserved for ipad
11 | reserved for ipad
12 | reserved for ipad
13 | reserved for ipad
14 | reserved for ipad
15 | reserved for ipad
16 | reserved for ipad
17 | reserved for ipad
18 | reserved for ipad
19 | reserved for ipad
20 | reserved for ipad
21 | reserved for ipad
22 | reserved for ipad
23 | goto #checkout
24 | goto #checkin
25
26 | function startup
27 | //send.modbus $dev=server $reg=0 $dec=0
28 | send.modbus $type=gsw $reg=15 $dec=80*10
29 | send.modbus $type=gsw $reg=16 $dec=30*10
30 | reuse #refresh_workflow_panels $sec=5
31 | reuse #gsw_motion_settings $sec=10
32 | wait $sec=5
33 | m_notify.set $dec=0
34 | exit
35
36
37 | function debugging
38 | debug
39 | exit
40
41
42 | function gsw_motion_settings
43 | send.modbus $dev=gsw1 $reg=300 $hex=63 //send GSW modbus [multi device]
44 | send.modbus $dev=gsw1 $reg=301 $hex=15E //send GSW modbus [multi device]
45 | send.modbus $dev=gsw1 $reg=302 $hex=04 //send GSW modbus [multi device]
46 | exit
47
48
49 | //function thermo_cycle
50 | //send.modbus $dev=server $reg=14 $len=16
51 | //exit
52
53 | //function dev_offline
54 | //send.modbus $dev=server $reg=8 $len=4
55 | //exit
56
57
58
59 | function checkout
60 | exit
61
62
63
64 | function checkin
65 | goto #checkout
66 | exit
67
68
69 | function GSW08_refresh | ok
70 | load $var=workflow
71 | If equal goto #4 $dec=7
72 | If equal goto #5 $dec=1
73 | load $hex=540455
74 | goto #4
75 | load $hex=540456
76 | goto #2
77 | load $hex=540465
78 | save $var=gs1
79 | math.and $hex=22
80 | send.modbus $dev=04 $reg=13 $len=4
81 | exit
82 | function GSW08_btn_1_dnd
83 | load $hex=540456
84 | send.modbus $dev=04 $reg=13 $len=4
85 | load $var=workflow
86 | If not equal goto #+5 $dec=7
87 | load $dec=0
88 | save $var=workflow
89 | load $hex=540455
90 | goto #+4
91 | load $dec=7
92 | save $var=workflow
93 | load $hex=540456
94 | send.modbus $dev=04 $reg=13 $len=4
95 | save $var=gs1
96 | reuse #GSW08_refresh $sec=15
97 | reuse #gsw05a_refresh
98 | reuse #gsw05b_refresh
99 | reuse #dnd_send
100 | exit
101 | function GSW08_btn_2
102 | reuse #entrance_master
103 | load $var=gs1
104 | math.and $hex=FFFFF3
105 | function GSW08_btn_common
106 | send.modbus $dev=04 $reg=13 $len=4
107 | wait $sec=0.15
108 | load $var=gs1
109 | send.modbus $dev=04 $reg=13 $len=4
110 | reuse #GSW08_refresh $sec=15
111 | exit
112 | function GSW08_btn_3_mur
113 | load $hex=540465
114 | send.modbus $dev=04 $reg=13 $len=4
115 | load $var=workflow
116 | If not equal goto #+5 $dec=1
117 | load $dec=0
118 | save $var=workflow
119 | load $hex=540455
120 | goto #+4
121 | load $dec=1
122 | save $var=workflow
123 | load $hex=540465
124 | send.modbus $dev=04 $reg=13 $len=4
125 | save $var=gs1
126 | reuse #GSW08_refresh $sec=15
127 | reuse #gsw05a_refresh
128 | reuse #gsw05b_refresh
129 | reuse #dnd_send
130 | exit
131 | function GSW08_btn_4
132 | reuse #entrance_relax
133 | load $var=gs1
134 | math.and $hex=FFFF3F
135 | goto #GSW08_btn_common
136 | function GSW08_btn_6
137 | reuse #entrance_living
138 | load $var=gs1
139 | math.and $hex=FFF3FF
140 | goto #GSW08_btn_common
141 | function GSW08_btn_10
142 | reuse #lounge_light
143 | load $var=gs1
144 | math.and $hex=F3FFFF
145 | goto #GSW08_btn_common
146 | function GSW08_btn_11
147 | reuse #kitchen_light
148 | load $var=gs1
149 | math.and $hex=CFFFFF
150 | goto #GSW08_btn_common
151 | function GSW08_btn_12
152 | reuse #dining_light
153 | load $var=gs1
154 | math.and $hex=3FFFFF
155 | goto #GSW08_btn_common
156
157
158
159
160 | function GSW05A_refresh | ok
161 | load $var=workflow
162 | If equal goto #3 $dec=7
163 | load $hex=11540
164 | goto #2
165 | load $hex=11580
166 | save $var=gs2
167 | math.and $hex=10080 //with night light
168 | send.modbus $dev=05 $reg=13 $len=4
169 | exit
170 | function GSW05A_btn_4_dnd
171 | load $hex=11580
172 | send.modbus $dev=05 $reg=13 $len=4
173 | load $var=workflow
174 | If not equal goto #+5 $dec=7
175 | load $dec=0
176 | save $var=workflow
177 | load $hex=11540
178 | goto #+4
179 | load $dec=7
180 | save $var=workflow
181 | load $hex=11580
182 | send.modbus $dev=05 $reg=13 $len=4
183 | save $var=gs2
184 | reuse #GSW05A_refresh $sec=15
185 | reuse #gsw08_refresh
186 | reuse #gsw05b_refresh
187 | reuse #dnd_send
188 | exit
189 | function GSW05A_btn_5
190 | reuse #master_bed_light
191 | load $var=gs2
192 | math.and $hex=FFFCFF
193 | function GSW05A_btn_common
194 | send.modbus $dev=05 $reg=13 $len=4
195 | wait $sec=0.15
196 | load $var=gs2
197 | send.modbus $dev=05 $reg=13 $len=4
198 | reuse #GSW05A_refresh $sec=15
199 | exit
200 | function GSW05A_btn_6
201 | reuse #master_bed_master
202 | load $var=gs2
203 | math.and $hex=FFF3FF
204 | goto #GSW05A_btn_common
205 | function GSW05A_btn_7
206 | reuse #master_bed_relax
207 | load $var=gs2
208 | math.and $hex=FFCFFF
209 | goto #GSW05A_btn_common
210 | function GSW05A_btn_9
211 | reuse #master_bed_night
212 | load $var=gs2
213 | math.and $hex=FCFFFF
214 | goto #GSW05A_btn_common
215
216
217
218
219 | function GSW05B_refresh | ok
220 | load $var=workflow
221 | If equal goto #3 $dec=7
222 | load $hex=11540
223 | goto #2
224 | load $hex=11580
225 | save $var=gs3
226 | math.and $hex=10080 //with night light
227 | send.modbus $dev=06 $reg=13 $len=4
228 | exit
229 | function GSW05B_btn_4_dnd
230 | load $hex=11580
231 | send.modbus $dev=06 $reg=13 $len=4
232 | load $var=workflow
233 | If not equal goto #+5 $dec=7
234 | load $dec=0
235 | save $var=workflow
236 | load $hex=11540
237 | goto #+4
238 | load $dec=7
239 | save $var=workflow
240 | load $hex=11580
241 | send.modbus $dev=06 $reg=13 $len=4
242 | save $var=gs3
243 | reuse #GSW05B_refresh $sec=15
244 | reuse #gsw08_refresh
245 | reuse #gsw05a_refresh
246 | reuse #dnd_send
247 | exit
248 | function GSW05B_btn_5
249 | reuse #master_bed_light
250 | load $var=gs3
251 | math.and $hex=FFFCFF
252 | function GSW05B_btn_common
253 | send.modbus $dev=06 $reg=13 $len=4
254 | wait $sec=0.15
255 | load $var=gs3
256 | send.modbus $dev=06 $reg=13 $len=4
257 | reuse #GSW05B_refresh $sec=15
258 | exit
259 | function GSW05B_btn_6
260 | reuse #master_bed_master
261 | load $var=gs3
262 | math.and $hex=FFF3FF
263 | goto #GSW05B_btn_common
264 | function GSW05B_btn_7
265 | reuse #master_bed_relax
266 | load $var=gs3
267 | math.and $hex=FFCFFF
268 | goto #GSW05B_btn_common
269 | function GSW05B_btn_9
270 | reuse #master_bed_night
271 | load $var=gs3
272 | math.and $hex=FCFFFF
273 | goto #GSW05B_btn_common
274
275
276
277
278
279
280
281
282 | function GSW04_refresh | ok
283 | load $dec=0
284 | send.modbus $dev=FE $reg=13 $len=4
285 | exit
286 | function GSW04_btn_4
287 | reuse #corridor_light
288 | load $hex=11400
289 | function GSW04_btn_common
290 | send.modbus $dev=FE $reg=13 $len=4
291 | wait $sec=0.15
292 | load $hex=11440
293 | send.modbus $dev=FE $reg=13 $len=4
294 | reuse #GSW04_refresh $sec=15
295 | exit
296 | function GSW04_btn_6
297 | reuse #living_room
298 | load $hex=11040
299 | goto #GSW04_btn_common
300 | function GSW04_btn_7
301 | reuse #storage1_light
302 | load $hex=10440
303 | goto #GSW04_btn_common
304 | function GSW04_btn_9
305 | reuse #storage2_light
306 | load $hex=1440
307 | goto #GSW04_btn_common
308
309
310
311
312
313 | function GSW03_refresh | ok
314 | load $bit=11 //night light icon
315 | send.modbus $dev=FE $reg=13 $len=4
316 | exit
317 | function GSW03_btn_4
318 | reuse #bath1_relax
319 | load $hex=500
320 | function GSW03_btn_common
321 | send.modbus $dev=FE $reg=13 $len=4
322 | wait $sec=0.15
323 | load $hex=540
324 | send.modbus $dev=FE $reg=13 $len=4
325 | reuse #GSW03_refresh $sec=15
326 | exit
327 | function GSW03_btn_5
328 | reuse #bath1_master
329 | load $hex=440
330 | goto #GSW03_btn_common
331 | function GSW03_btn_6
332 | reuse #bath1_night
333 | load $hex=140
334 | goto #GSW03_btn_common
335
336
337
338
339 | function GSW02_refresh | ok
340 | load $dec=0
341 | send.modbus $dev=FE $reg=13 $len=4
342 | exit
343 | function GSW02_btn_4
344 | reuse #bed1_relax
345 | load $hex=400
346 | function GSW02_btn_common
347 | send.modbus $dev=FE $reg=13 $len=4
348 | wait $sec=0.15
349 | load $hex=440
350 | send.modbus $dev=FE $reg=13 $len=4
351 | reuse #GSW02_refresh $sec=15
352 | exit
353 | function GSW02_btn_6
354 | reuse #bed1_light
355 | load $hex=40
356 | goto #GSW02_btn_common
357
358
359
360
361
362
363
364
365
366
367
368 | //motion functions
369
370 | function pir1_close | ok
371 | reuse #pir1_open $sec=15
372 | reuse #rcu_main_motion_close
373 | exit
374
375
376
377 | function pir1_open | ok
378 | reuse #rcu_main_motion_open
379 | exit
380
381
382 | function rcu_main_motion_close | ok
383 | load modbus $var=m_motion
384 | if equal #exit $dec=1
385 | m_motion.set $dec=1
386 | exit
387
388
389 | function rcu_main_motion_open | ok
390 | load modbus $var=m_motion
391 | if equal #exit $dec=0
392 | m_motion.unset
393 | exit
394
395
396
397
398
399
400
401
402
403 | //send modbus
404
405
406 | function dnd_send | ok
407 | load $var=workflow
408 | save modbus $var=m_workflow
409 | exit
410
411
412 | function send_rcu_relays | ok
413 | reuse #use_send_rcu_relays $sec=1
414 | exit
415 | function use_send_rcu_relays
416 | rcu.read relays
417 | save modbus $var=m_rcu_relays
418 | exit
419
420
421
422 | function master_bed_master | ok
423 | m_master_bed_panel.set $dec=1
424 | exit
425
426
427 | function master_bed_relax | ok
428 | m_master_bed_panel.set $dec=2
429 | exit
430
431
432 | function master_bed_night | ok
433 | m_master_bed_panel.set $dec=3
434 | exit
435
436
437 | function master_bed_light | ok
438 | m_master_bed_panel.set $dec=4
439 | exit
440
441
442
443 | function bed1_relax | ok
444 | m_bed1_panel.set $dec=1
445 | exit
446
447 | function bed1_light | ok
448 | m_bed1_panel.set $dec=2
449 | exit
450
451
452 | function bath1_relax | ok
453 | m_bath1_panel.set $dec=1
454 | exit
455
456
457 | function bath1_master | ok
458 | m_bath1_panel.set $dec=2
459 | exit
460
461
462 | function bath1_night | ok
463 | m_bath1_panel.set $dec=3
464 | exit
465
466
467
468 | function entrance_master | ok
469 | m_entrance_panel.set $dec=1
470 | exit
471
472
473 | function entrance_relax | ok
474 | m_entrance_panel.set $dec=2
475 | exit
476
477
478 | function entrance_living | ok
479 | m_entrance_panel.set $dec=3
480 | exit
481
482
483 | function lounge_light | ok
484 | m_entrance_panel.set $dec=4
485 | exit
486
487
488 | function kitchen_light | ok
489 | m_entrance_panel.set $dec=5
490 | exit
491
492
493 | function dining_light | ok
494 | m_entrance_panel.set $dec=6
495 | exit
496
497
498
499 | function corridor_light | ok
500 | m_corridor_panel.set $dec=1
501 | exit
502
503
504 | function living_room | ok
505 | m_corridor_panel.set $dec=2
506 | exit
507
508
509 | function storage1_light | ok
510 | m_corridor_panel.set $dec=3
511 | exit
512
513
514 | function storage2_light | ok
515 | m_corridor_panel.set $dec=4
516 | exit
517
518
519
520
521
522
523
524
525 | //receive modbus
526
527
528 | function modbus_manager
529 | if equal #modbus_user_receive $dec=0
530 | if equal #modbus_workflow_receive $dec=1
531 | if equal #receive_rcu_relays $dec=2
532 | exit
533
534
535 | function modbus_user_receive
536 | load modbus $var=m_user
537 | save $var=user
538 | exit
539
540
541 | function modbus_workflow_receive
542 | load modbus $var=m_workflow
543 | save $var=workflow
544 | function refresh_workflow_panels
545 | reuse #gsw08_refresh
546 | reuse #gsw05a_refresh
547 | reuse #gsw05b_refresh
548 | exit
549
550
551
552 | function receive_rcu_relays
553 | load modbus $var=m_rcu_relays
554 | rcu.set all relays from acc
555 | exit
556
557
558
559
560
561
562
563
564
565
566
567

## Program3
| ; |  | Dir: | C:\tini\ModularHotel\ABSlink\RCUmanager\bin\Release
| ;code |  | # | Description | done | Parameters (8 bytes)
0000 | 19 00 00 00 00 00 00 00; | #startup | 0x01 | GoTo & Wait | d | 0x01 | wait # tick |  | 2bytete optional goto |  |  | tick | [5 empty] | 00=nogoto 00=nowait
0001 | 00 00 00 00 09 2E ED 09; | version [35561452341814213551145390817034,9] |  |  | d | 0x03 | WaitTick/OrigDev |  | 2byte goto (acc->acc called) |  |  | tick | Relative, reuse of existing task with same device if present updating tick (used for timeout interactive mode) [multidev]
0002 | 01 01 21 00 00 00 00 00; | goto #debugging | 0x0a | Wait absolute | d | 1=value,3=1B,4=2B, 5=4B,a=acc[0]=RTC(add), |  |  |  |  | 2 byte empty |  |  |  | 4 byte value |  | 3-5= addr a-b uses RTC+acc[0]
0003 | 01 01 00 00 00 00 00 00; | reserved for ipad | 0x02 | Rcu Hardware | d | 0x01 | set relay |  | 0=accum, 1=value, 3=add1B, 4=add2B, 5=add4B | [5 empty] | byte low bitmap from relay 1 to 8
0004 | 01 01 00 00 00 00 00 00; | reserved for ipad |  |  | d | 0x02 | unset relay |  | 0=accum, 1=value, 3=add1B, 4=add2B, 5=add4B | [5 empty] | byte low bitmap from relay 1 to 8
0005 | 01 01 00 00 00 00 00 00; | reserved for ipad |  |  | d | 0x03 | read relays in accumulator
0006 | 01 01 00 00 00 00 00 00; | reserved for ipad |  |  | d | 0x04 | set all relays |  | 0=accum, 1=value, 3=add1B, 4=add2B, 5=add4B | [5 empty] | bitmap
0007 | 01 01 00 00 00 00 00 00; | reserved for ipad |  |  | d | 0x05 | set OUT Lock % |  | 0=accum, 1=value, 3=add1B, 4=add2B, 5=add4B | [5 empty] | 50% = 12Volt
0008 | 01 01 00 00 00 00 00 00; | reserved for ipad |  |  | d | 0x06 | set 0-10 V [1] |  | 0=accum, 1=value, 3=add1B, 4=add2B, 5=add4B
0009 | 01 01 00 00 00 00 00 00; | reserved for ipad |  |  | d | 0x07 | set 0-10 V [2] |  | 0=accum, 1=value, 3=add1B, 4=add2B, 5=add4B
000A | 01 01 00 00 00 00 00 00; | reserved for ipad |  |  |  | 0x08 | Input->Accumulator |  | Input # |  |  | Get inputs value in accumulator, if par1=0 all inputs (bitmap)
000B | 01 01 00 00 00 00 00 00; | reserved for ipad |  |  | d | 0x09 | set on relays |  | 0=accum, 1=value, 3=add1B, 4=add2B, 5=add4B | [5 empty] | bitmap
000C | 01 01 00 00 00 00 00 00; | reserved for ipad |  |  | d | 0x0a | set off relays |  | 0=accum, 1=value, 3=add1B, 4=add2B, 5=add4B | [5 empty] | bitmap
000D | 01 01 00 00 00 00 00 00; | reserved for ipad |  |  | d | 0x0b | xor relays |  | 0=accum, 1=value, 3=add1B, 4=add2B, 5=add4B | [5 empty] | bitmap
000E | 01 01 00 00 00 00 00 00; | reserved for ipad | 0x03 | Run task | d | 0x01 | NewTask Wait # tick |  | 2byte goto |  |  | tick | Run a separate thread
000F | 01 01 00 00 00 00 00 00; | reserved for ipad |  |  | d | 0x02 | Reuse Wait # tick |  | 2byte goto (acc->acc called) |  |  | tick | Relative, reuse of existing task if present updating tick (used for timeout interactive mode)
0010 | 01 01 00 00 00 00 00 00; | reserved for ipad |  |  | d | 0x03 | Reuse/WaitTick/OrigDev |  | 2byte goto (acc->acc called) |  |  | tick | Relative, reuse of existing task with same device if present updating tick (used for timeout interactive mode) [multidev]
0011 | 01 01 00 00 00 00 00 00; | reserved for ipad | 0x04 | Exit | d | 0x01 | Stop execution
0012 | 01 01 00 00 00 00 00 00; | reserved for ipad |  |  |  | 0x02 | Return to caller in accumulator
0013 | 01 01 00 00 00 00 00 00; | reserved for ipad | 0x05 | GoTo if acc[0] != | d |  | 0=acc, 1=value, 3=addr 1B, 4=addr 2B, 5=addr 4B | [6 empty] | 2byte goto |  | 4bytes value
0014 | 01 01 00 00 00 00 00 00; | reserved for ipad | 0x06 | GoTo if acc[0] > | d |  | 0=acc, 1=value, 3=addr 1B, 4=addr 2B, 5=addr 4B | [6 empty] | 2byte goto |  | 4bytes value
0015 | 01 01 00 00 00 00 00 00; | reserved for ipad | 0x07 | GoTo if acc[0] < | d |  | 0=acc, 1=value, 3=addr 1B, 4=addr 2B, 5=addr 4B | [6 empty] | 2byte goto |  | 4bytes value
0016 | 01 01 00 00 00 00 00 00; | reserved for ipad | 0x08 | GoTo if acc[0] = | d |  | 0=acc, 1=value, 3=addr 1B, 4=addr 2B, 5=addr 4B | [6 empty] | 2byte goto |  | 4bytes value
0017 | 01 01 27 00 00 00 00 00; | goto #checkout | 0x09 | GoTo if acc[0] AND | d |  | 0=acc, 1=value, 3=addr 1B, 4=addr 2B, 5=addr 4B | [6 empty] | 2byte goto |  | 4bytes value |  |  | goto if a bit match
0018 | 01 01 28 00 00 00 00 00; | goto #checkin | 0x10 | Mathematics | d | 0x01 | Add | 1=value, 2=RPN, 3=addr 1B, 4=addr 2B, 5=addr 4B | [5 empty] | empty | 4 byte value |  | 1 value is from last 4 bytes
0019 | 21 06 00 0F 03 20 00 00; | send.modbus $type=gsw $reg=15 $dec=80*10 |  |  | d | 0x02 | Sub | 1=value, 2=RPN, 3=addr 1B, 4=addr 2B, 5=addr 4B | [5 empty] | empty | 4 byte value |  | 2 RPN operates in Accumulator and last stack, shift down 3 values in stack
001A | 21 06 00 10 01 2C 00 00; | send.modbus $type=gsw $reg=16 $dec=30*10 |  |  | d | 0x03 | Mul | 1=value, 2=RPN, 3=addr 1B, 4=addr 2B, 5=addr 4B | [5 empty] | empty | 4 byte value |  | 3-5 uses memory with 1,2,4 bytes
001B | 03 02 63 01 50 C3 00 00; | reuse #refresh_workflow_panels $sec=5 |  |  | d | 0x04 | OR | 1=value, 2=RPN, 3=addr 1B, 4=addr 2B, 5=addr 4B | [5 empty] | empty | 4 byte value
001C | 03 02 23 00 A0 86 01 00; | reuse #gsw_motion_settings $sec=10 |  |  | d | 0x05 | XOR | 1=value, 2=RPN, 3=addr 1B, 4=addr 2B, 5=addr 4B | [5 empty] | empty | 4 byte value |  | Stack is 3 values + Accumulator like Forth
001D | 01 01 00 00 50 C3 00 00; | wait $sec=5 |  |  | d | 0x06 | AND | 1=value, 2=RPN, 3=addr 1B, 4=addr 2B, 5=addr 4B | [5 empty] | empty | 4 byte value
001E | 10 80 01 00 00 00 00 00; | load $dec=0 |  |  | d | 0x07 | << | 1=value, 2=RPN, 3=addr 1B, 4=addr 2B, 5=addr 4B | [5 empty] | empty | 4 byte value
001F | 10 81 12 00 09 00 00 00; | save modbus $var=m_notify |  |  | d | 0x08 | >> | 1=value, 2=RPN, 3=addr 1B, 4=addr 2B, 5=addr 4B | [5 empty] | empty | 4 byte value |  |  | 1B=byte, 2B=16bit, 4B=32bit
0020 | 04 01 00 00 00 00 00 00; | exit |  |  | d | 0x09 | Div | 0=Acc, 1=value, 2=RPN, 3=addr 1B, 4=addr 2B, 5=addr 4B | [5 empty] | empty | 4 byte value |  | 3-5 uses memory with 1,2,4 bytes
0021 | 40 01 01 00 00 00 00 00; | debug |  |  | d | 0x0a | Mod | 0=Acc, 1=value, 2=RPN, 3=addr 1B, 4=addr 2B, 5=addr 4B | [5 empty] | empty | 4 byte value |  | 3-5 uses memory with 1,2,4 bytes
0022 | 04 01 00 00 00 00 00 00; | exit |  |  | d | 0x80 | PUSH | 1=value,3=1B,4=2B, 5=4B,a=acc[0]=RTC(add), | [5 empty] | shiftYN | 4 byte value |  | 3-5= addr a-b uses RTC+acc[0]
0023 | 20 04 01 2C 00 63 00 00; | send.modbus $dev=gsw1 $reg=300 $hex=63 |  |  | d | [8 empty] | shiftYN | 1 item size |  | 1 byte relative positive address, 1 elements, 1 empty
0024 | 20 04 01 2D 01 5E 00 00; | send.modbus $dev=gsw1 $reg=301 $hex=15e |  |  | d | [8 empty] | shiftYN | 1 item size |  | 1 byte relative positive address, 1 elements, 1 empty
0025 | 20 04 01 2E 00 04 00 00; | send.modbus $dev=gsw1 $reg=302 $hex=04 |  |  | d |  |  | e=CurrentEventDevice, f=addr 4B+OrigDevEnum(DeviceMap) | [5 empty] | shiftYN | 4 byte value
0026 | 04 01 00 00 00 00 00 00; | exit |  |  | d | 0x81 | POP | 3=1B,4=2B,5=4B,a=RTC(add)=acc[0],b=RTC(acc[0])=acc[1] | [5 empty] | shiftYN | 4 byte value
0027 | 04 01 00 00 00 00 00 00; | exit |  |  | d |  |  | e=CurrentEventDevice, f=addr 4B+OrigDevEnum(DeviceMap) | [5 empty] | shiftYN | 4 byte value
0028 | 01 01 27 00 00 00 00 00; | goto #checkout |  |  | d | 0x82 | PUSH time | [6 empty] | shiftYN
0029 | 04 01 00 00 00 00 00 00; | exit | 0x20 | Send ModBus 1 Word | d | Dest | PosHi | PosLo | Whi | Wlo | crcH | crcL |  | Dest FF=ServerIP, FE=OrigDevice |  |  |  |  | # dev map (Type=all devices with specified type)
002A | 10 80 0A 00 16 00 00 00; | load $var=workflow | 0x21 | Send ModBus 1 Word | d | Type | PosHi | PosLo | Whi | Wlo | crcH | crcL |  | Dest FF=ServerIP, FE=OrigDevice |  |  |  |  | Send to all devices with type=x
002B | 08 01 2F 00 07 00 00 00; | if equal goto #4 $dec=7 | 0x22 | Send ModBus Accumulator | d | Dest | PosHi | PosLo | bytes(2-16),NW |  | crcH | crcL |  | Dest FF=ServerIP, FE=OrigDevice |  |  |  |  | NW=no wait
002C | 08 01 31 00 01 00 00 00; | if equal goto #5 $dec=1 | 0x23 | Send ModBus Accumulator | d | Type | PosHi | PosLo | bytes(2-16),00 |  | crcH | crcL |  | Dest FF=ServerIP, FE=OrigDevice |  |  |  |  | Send to all devices with type=x
002D | 10 80 01 00 55 04 54 00; | load $hex=540455 | 0x26 | Read modbus in Accumulator | d | Dest | PosHi | PosLo | bytes(2,4), 00 |  | crcH | crcL |  | Dest FF=ServerIP, FE=OrigDevice
002E | 01 01 32 00 00 00 00 00; | goto #4 | 0x2a | Seand modbus Acc[*] | d d d: d; PUSH time Whi Whi: Dest+PosH+PosL+Len (1b+1b+1b+1b+max 12b max message) |  | gateway |  | 02190003;c8 TAG SetPoint=200 ->35192835;200;0;0
002F | 10 80 01 00 56 04 54 00; | load $hex=540456 | 0x2b | Read modbus Acc[0]->Acc[*] | d d d: d; PUSH time Whi Whi: Dest+PosH+PosL+Len |  | gateway |  | Reat TAG Setpoint 35192835;0;0;0
0030 | 01 01 32 00 00 00 00 00; | goto #2 | 0x30 | Call RCU Acc[*] | 0x82 Dest Type: Dest; PUSH time Whi Whi: Program address |  | Pass 4 register to the defined RCU device (+read ModBus 3 su TCP/IP)
0031 | 10 80 01 00 65 04 54 00; | load $hex=540465
0032 | 10 81 0A 00 17 00 00 00; | save $var=gs1 | # | Notify packet | d d d: Parameters
0033 | 10 06 01 00 22 00 00 00; | math.and $hex=22 | 1 | Eartbeat | d d d: Counter
0034 | 22 04 00 0D 04 00 00 00; | send.modbus $dev=04 $reg=13 $len=4 | 2 | Card Insert | d d d: CardId (8), Time
0035 | 04 01 00 00 00 00 00 00; | exit | 3 | CardExtract | d d d: none
0036 | 10 80 01 00 56 04 54 00; | load $hex=540456 | 4 | Mur/Dnd | d d d: Status
0037 | 22 04 00 0D 04 00 00 00; | send.modbus $dev=04 $reg=13 $len=4 | 5 | OpenNOK | d d d: Status, Time
0038 | 10 80 0A 00 16 00 00 00; | load $var=workflow | 6 | Open OK | d d d: CardId (8), Time
0039 | 05 01 3E 00 07 00 00 00; | if not equal goto #+5 $dec=7 | 7 | Read RTC Var | bar: d d d to PUSH time PosLo PosLo
003A | 10 80 01 00 00 00 00 00; | load $dec=0 | 8 | Read modbus from device | bar: d d d to PUSH time PosLo PosLo
003B | 10 81 0A 00 16 00 00 00; | save $var=workflow | bar: d d d to PUSH time PosLo PosLo
003C | 10 80 01 00 55 04 54 00; | load $hex=540455 | bar: d d d to PUSH time PosLo PosLo
003D | 01 01 41 00 00 00 00 00; | goto #+4 | bar: d d d to PUSH time PosLo PosLo
003E | 10 80 01 00 07 00 00 00; | load $dec=7
003F | 10 81 0A 00 16 00 00 00; | save $var=workflow
0040 | 10 80 01 00 56 04 54 00; | load $hex=540456
0041 | 22 04 00 0D 04 00 00 00; | send.modbus $dev=04 $reg=13 $len=4
0042 | 10 81 0A 00 17 00 00 00; | save $var=gs1
0043 | 03 02 2A 00 F0 49 02 00; | reuse #gsw08_refresh $sec=15
0044 | 03 02 77 00 00 00 00 00; | reuse #gsw05a_refresh
0045 | 03 02 A7 00 00 00 00 00; | reuse #gsw05b_refresh
0046 | 03 02 19 01 00 00 00 00; | reuse #dnd_send
0047 | 04 01 00 00 00 00 00 00; | exit
0048 | 03 02 3C 01 00 00 00 00; | reuse #entrance_master
0049 | 10 80 0A 00 17 00 00 00; | load $var=gs1
004A | 10 06 01 00 F3 FF FF 00; | math.and $hex=fffff3
004B | 22 04 00 0D 04 00 00 00; | send.modbus $dev=04 $reg=13 $len=4
004C | 01 01 00 00 DC 05 00 00; | wait $sec=0.15
004D | 10 80 0A 00 17 00 00 00; | load $var=gs1
004E | 22 04 00 0D 04 00 00 00; | send.modbus $dev=04 $reg=13 $len=4
004F | 03 02 2A 00 F0 49 02 00; | reuse #gsw08_refresh $sec=15
0050 | 04 01 00 00 00 00 00 00; | exit
0051 | 10 80 01 00 65 04 54 00; | load $hex=540465
0052 | 22 04 00 0D 04 00 00 00; | send.modbus $dev=04 $reg=13 $len=4
0053 | 10 80 0A 00 16 00 00 00; | load $var=workflow
0054 | 05 01 59 00 01 00 00 00; | if not equal goto #+5 $dec=1
0055 | 10 80 01 00 00 00 00 00; | load $dec=0
0056 | 10 81 0A 00 16 00 00 00; | save $var=workflow
0057 | 10 80 01 00 55 04 54 00; | load $hex=540455
0058 | 01 01 5C 00 00 00 00 00; | goto #+4
0059 | 10 80 01 00 01 00 00 00; | load $dec=1
005A | 10 81 0A 00 16 00 00 00; | save $var=workflow
005B | 10 80 01 00 65 04 54 00; | load $hex=540465
005C | 22 04 00 0D 04 00 00 00; | send.modbus $dev=04 $reg=13 $len=4
005D | 10 81 0A 00 17 00 00 00; | save $var=gs1
005E | 03 02 2A 00 F0 49 02 00; | reuse #gsw08_refresh $sec=15
005F | 03 02 77 00 00 00 00 00; | reuse #gsw05a_refresh
0060 | 03 02 A7 00 00 00 00 00; | reuse #gsw05b_refresh
0061 | 03 02 19 01 00 00 00 00; | reuse #dnd_send
0062 | 04 01 00 00 00 00 00 00; | exit
0063 | 03 02 3F 01 00 00 00 00; | reuse #entrance_relax
0064 | 10 80 0A 00 17 00 00 00; | load $var=gs1
0065 | 10 06 01 00 3F FF FF 00; | math.and $hex=ffff3f
0066 | 01 01 4B 00 00 00 00 00; | goto #gsw08_btn_common
0067 | 03 02 42 01 00 00 00 00; | reuse #entrance_living
0068 | 10 80 0A 00 17 00 00 00; | load $var=gs1
0069 | 10 06 01 00 FF F3 FF 00; | math.and $hex=fff3ff
006A | 01 01 4B 00 00 00 00 00; | goto #gsw08_btn_common
006B | 03 02 45 01 00 00 00 00; | reuse #lounge_light
006C | 10 80 0A 00 17 00 00 00; | load $var=gs1
006D | 10 06 01 00 FF FF F3 00; | math.and $hex=f3ffff
006E | 01 01 4B 00 00 00 00 00; | goto #gsw08_btn_common
006F | 03 02 48 01 00 00 00 00; | reuse #kitchen_light
0070 | 10 80 0A 00 17 00 00 00; | load $var=gs1
0071 | 10 06 01 00 FF FF CF 00; | math.and $hex=cfffff
0072 | 01 01 4B 00 00 00 00 00; | goto #gsw08_btn_common
0073 | 03 02 4B 01 00 00 00 00; | reuse #dining_light
0074 | 10 80 0A 00 17 00 00 00; | load $var=gs1
0075 | 10 06 01 00 FF FF 3F 00; | math.and $hex=3fffff
0076 | 01 01 4B 00 00 00 00 00; | goto #gsw08_btn_common
0077 | 10 80 0A 00 16 00 00 00; | load $var=workflow
0078 | 08 01 7B 00 07 00 00 00; | if equal goto #3 $dec=7
0079 | 10 80 01 00 40 15 01 00; | load $hex=11540
007A | 01 01 7C 00 00 00 00 00; | goto #2
007B | 10 80 01 00 80 15 01 00; | load $hex=11580
007C | 10 81 0A 00 18 00 00 00; | save $var=gs2
007D | 10 06 01 00 80 00 01 00; | math.and $hex=10080
007E | 22 05 00 0D 04 00 00 00; | send.modbus $dev=05 $reg=13 $len=4
007F | 04 01 00 00 00 00 00 00; | exit
0080 | 10 80 01 00 80 15 01 00; | load $hex=11580
0081 | 22 05 00 0D 04 00 00 00; | send.modbus $dev=05 $reg=13 $len=4
0082 | 10 80 0A 00 16 00 00 00; | load $var=workflow
0083 | 05 01 88 00 07 00 00 00; | if not equal goto #+5 $dec=7
0084 | 10 80 01 00 00 00 00 00; | load $dec=0
0085 | 10 81 0A 00 16 00 00 00; | save $var=workflow
0086 | 10 80 01 00 40 15 01 00; | load $hex=11540
0087 | 01 01 8B 00 00 00 00 00; | goto #+4
0088 | 10 80 01 00 07 00 00 00; | load $dec=7
0089 | 10 81 0A 00 16 00 00 00; | save $var=workflow
008A | 10 80 01 00 80 15 01 00; | load $hex=11580
008B | 22 05 00 0D 04 00 00 00; | send.modbus $dev=05 $reg=13 $len=4
008C | 10 81 0A 00 18 00 00 00; | save $var=gs2
008D | 03 02 77 00 F0 49 02 00; | reuse #gsw05a_refresh $sec=15
008E | 03 02 2A 00 00 00 00 00; | reuse #gsw08_refresh
008F | 03 02 A7 00 00 00 00 00; | reuse #gsw05b_refresh
0090 | 03 02 19 01 00 00 00 00; | reuse #dnd_send
0091 | 04 01 00 00 00 00 00 00; | exit
0092 | 03 02 2A 01 00 00 00 00; | reuse #master_bed_light
0093 | 10 80 0A 00 18 00 00 00; | load $var=gs2
0094 | 10 06 01 00 FF FC FF 00; | math.and $hex=fffcff
0095 | 22 05 00 0D 04 00 00 00; | send.modbus $dev=05 $reg=13 $len=4
0096 | 01 01 00 00 DC 05 00 00; | wait $sec=0.15
0097 | 10 80 0A 00 18 00 00 00; | load $var=gs2
0098 | 22 05 00 0D 04 00 00 00; | send.modbus $dev=05 $reg=13 $len=4
0099 | 03 02 77 00 F0 49 02 00; | reuse #gsw05a_refresh $sec=15
009A | 04 01 00 00 00 00 00 00; | exit
009B | 03 02 21 01 00 00 00 00; | reuse #master_bed_master
009C | 10 80 0A 00 18 00 00 00; | load $var=gs2
009D | 10 06 01 00 FF F3 FF 00; | math.and $hex=fff3ff
009E | 01 01 95 00 00 00 00 00; | goto #gsw05a_btn_common
009F | 03 02 24 01 00 00 00 00; | reuse #master_bed_relax
00A0 | 10 80 0A 00 18 00 00 00; | load $var=gs2
00A1 | 10 06 01 00 FF CF FF 00; | math.and $hex=ffcfff
00A2 | 01 01 95 00 00 00 00 00; | goto #gsw05a_btn_common
00A3 | 03 02 27 01 00 00 00 00; | reuse #master_bed_night
00A4 | 10 80 0A 00 18 00 00 00; | load $var=gs2
00A5 | 10 06 01 00 FF FF FC 00; | math.and $hex=fcffff
00A6 | 01 01 95 00 00 00 00 00; | goto #gsw05a_btn_common
00A7 | 10 80 0A 00 16 00 00 00; | load $var=workflow
00A8 | 08 01 AB 00 07 00 00 00; | if equal goto #3 $dec=7
00A9 | 10 80 01 00 40 15 01 00; | load $hex=11540
00AA | 01 01 AC 00 00 00 00 00; | goto #2
00AB | 10 80 01 00 80 15 01 00; | load $hex=11580
00AC | 10 81 0A 00 19 00 00 00; | save $var=gs3
00AD | 10 06 01 00 80 00 01 00; | math.and $hex=10080
00AE | 22 06 00 0D 04 00 00 00; | send.modbus $dev=06 $reg=13 $len=4
00AF | 04 01 00 00 00 00 00 00; | exit
00B0 | 10 80 01 00 80 15 01 00; | load $hex=11580
00B1 | 22 06 00 0D 04 00 00 00; | send.modbus $dev=06 $reg=13 $len=4
00B2 | 10 80 0A 00 16 00 00 00; | load $var=workflow
00B3 | 05 01 B8 00 07 00 00 00; | if not equal goto #+5 $dec=7
00B4 | 10 80 01 00 00 00 00 00; | load $dec=0
00B5 | 10 81 0A 00 16 00 00 00; | save $var=workflow
00B6 | 10 80 01 00 40 15 01 00; | load $hex=11540
00B7 | 01 01 BB 00 00 00 00 00; | goto #+4
00B8 | 10 80 01 00 07 00 00 00; | load $dec=7
00B9 | 10 81 0A 00 16 00 00 00; | save $var=workflow
00BA | 10 80 01 00 80 15 01 00; | load $hex=11580
00BB | 22 06 00 0D 04 00 00 00; | send.modbus $dev=06 $reg=13 $len=4
00BC | 10 81 0A 00 19 00 00 00; | save $var=gs3
00BD | 03 02 A7 00 F0 49 02 00; | reuse #gsw05b_refresh $sec=15
00BE | 03 02 2A 00 00 00 00 00; | reuse #gsw08_refresh
00BF | 03 02 77 00 00 00 00 00; | reuse #gsw05a_refresh
00C0 | 03 02 19 01 00 00 00 00; | reuse #dnd_send
00C1 | 04 01 00 00 00 00 00 00; | exit
00C2 | 03 02 2A 01 00 00 00 00; | reuse #master_bed_light
00C3 | 10 80 0A 00 19 00 00 00; | load $var=gs3
00C4 | 10 06 01 00 FF FC FF 00; | math.and $hex=fffcff
00C5 | 22 06 00 0D 04 00 00 00; | send.modbus $dev=06 $reg=13 $len=4
00C6 | 01 01 00 00 DC 05 00 00; | wait $sec=0.15
00C7 | 10 80 0A 00 19 00 00 00; | load $var=gs3
00C8 | 22 06 00 0D 04 00 00 00; | send.modbus $dev=06 $reg=13 $len=4
00C9 | 03 02 A7 00 F0 49 02 00; | reuse #gsw05b_refresh $sec=15
00CA | 04 01 00 00 00 00 00 00; | exit
00CB | 03 02 21 01 00 00 00 00; | reuse #master_bed_master
00CC | 10 80 0A 00 19 00 00 00; | load $var=gs3
00CD | 10 06 01 00 FF F3 FF 00; | math.and $hex=fff3ff
00CE | 01 01 C5 00 00 00 00 00; | goto #gsw05b_btn_common
00CF | 03 02 24 01 00 00 00 00; | reuse #master_bed_relax
00D0 | 10 80 0A 00 19 00 00 00; | load $var=gs3
00D1 | 10 06 01 00 FF CF FF 00; | math.and $hex=ffcfff
00D2 | 01 01 C5 00 00 00 00 00; | goto #gsw05b_btn_common
00D3 | 03 02 27 01 00 00 00 00; | reuse #master_bed_night
00D4 | 10 80 0A 00 19 00 00 00; | load $var=gs3
00D5 | 10 06 01 00 FF FF FC 00; | math.and $hex=fcffff
00D6 | 01 01 C5 00 00 00 00 00; | goto #gsw05b_btn_common
00D7 | 10 80 01 00 00 00 00 00; | load $dec=0
00D8 | 22 FE 00 0D 04 00 00 00; | send.modbus $dev=fe $reg=13 $len=4
00D9 | 04 01 00 00 00 00 00 00; | exit
00DA | 03 02 4E 01 00 00 00 00; | reuse #corridor_light
00DB | 10 80 01 00 00 14 01 00; | load $hex=11400
00DC | 22 FE 00 0D 04 00 00 00; | send.modbus $dev=fe $reg=13 $len=4
00DD | 01 01 00 00 DC 05 00 00; | wait $sec=0.15
00DE | 10 80 01 00 40 14 01 00; | load $hex=11440
00DF | 22 FE 00 0D 04 00 00 00; | send.modbus $dev=fe $reg=13 $len=4
00E0 | 03 02 D7 00 F0 49 02 00; | reuse #gsw04_refresh $sec=15
00E1 | 04 01 00 00 00 00 00 00; | exit
00E2 | 03 02 51 01 00 00 00 00; | reuse #living_room
00E3 | 10 80 01 00 40 10 01 00; | load $hex=11040
00E4 | 01 01 DC 00 00 00 00 00; | goto #gsw04_btn_common
00E5 | 03 02 54 01 00 00 00 00; | reuse #storage1_light
00E6 | 10 80 01 00 40 04 01 00; | load $hex=10440
00E7 | 01 01 DC 00 00 00 00 00; | goto #gsw04_btn_common
00E8 | 03 02 57 01 00 00 00 00; | reuse #storage2_light
00E9 | 10 80 01 00 40 14 00 00; | load $hex=1440
00EA | 01 01 DC 00 00 00 00 00; | goto #gsw04_btn_common
00EB | 10 80 01 00 00 04 00 00; | load $bit=11
00EC | 22 FE 00 0D 04 00 00 00; | send.modbus $dev=fe $reg=13 $len=4
00ED | 04 01 00 00 00 00 00 00; | exit
00EE | 03 02 33 01 00 00 00 00; | reuse #bath1_relax
00EF | 10 80 01 00 00 05 00 00; | load $hex=500
00F0 | 22 FE 00 0D 04 00 00 00; | send.modbus $dev=fe $reg=13 $len=4
00F1 | 01 01 00 00 DC 05 00 00; | wait $sec=0.15
00F2 | 10 80 01 00 40 05 00 00; | load $hex=540
00F3 | 22 FE 00 0D 04 00 00 00; | send.modbus $dev=fe $reg=13 $len=4
00F4 | 03 02 EB 00 F0 49 02 00; | reuse #gsw03_refresh $sec=15
00F5 | 04 01 00 00 00 00 00 00; | exit
00F6 | 03 02 36 01 00 00 00 00; | reuse #bath1_master
00F7 | 10 80 01 00 40 04 00 00; | load $hex=440
00F8 | 01 01 F0 00 00 00 00 00; | goto #gsw03_btn_common
00F9 | 03 02 39 01 00 00 00 00; | reuse #bath1_night
00FA | 10 80 01 00 40 01 00 00; | load $hex=140
00FB | 01 01 F0 00 00 00 00 00; | goto #gsw03_btn_common
00FC | 10 80 01 00 00 00 00 00; | load $dec=0
00FD | 22 FE 00 0D 04 00 00 00; | send.modbus $dev=fe $reg=13 $len=4
00FE | 04 01 00 00 00 00 00 00; | exit
00FF | 03 02 2D 01 00 00 00 00; | reuse #bed1_relax
0100 | 10 80 01 00 00 04 00 00; | load $hex=400
0101 | 22 FE 00 0D 04 00 00 00; | send.modbus $dev=fe $reg=13 $len=4
0102 | 01 01 00 00 DC 05 00 00; | wait $sec=0.15
0103 | 10 80 01 00 40 04 00 00; | load $hex=440
0104 | 22 FE 00 0D 04 00 00 00; | send.modbus $dev=fe $reg=13 $len=4
0105 | 03 02 FC 00 F0 49 02 00; | reuse #gsw02_refresh $sec=15
0106 | 04 01 00 00 00 00 00 00; | exit
0107 | 03 02 30 01 00 00 00 00; | reuse #bed1_light
0108 | 10 80 01 00 40 00 00 00; | load $hex=40
0109 | 01 01 01 01 00 00 00 00; | goto #gsw02_btn_common
010A | 03 02 0D 01 F0 49 02 00; | reuse #pir1_open $sec=15
010B | 03 02 0F 01 00 00 00 00; | reuse #rcu_main_motion_close
010C | 04 01 00 00 00 00 00 00; | exit
010D | 03 02 14 01 00 00 00 00; | reuse #rcu_main_motion_open
010E | 04 01 00 00 00 00 00 00; | exit
010F | 10 80 12 00 08 00 00 00; | load modbus $var=m_motion
0110 | 08 01 13 01 01 00 00 00; | if equal #exit $dec=1
0111 | 10 80 01 00 01 00 00 00; | load $dec=1
0112 | 10 81 12 00 08 00 00 00; | save modbus $var=m_motion
0113 | 04 01 00 00 00 00 00 00; | exit
0114 | 10 80 12 00 08 00 00 00; | load modbus $var=m_motion
0115 | 08 01 18 01 00 00 00 00; | if equal #exit $dec=0
0116 | 10 80 01 00 00 00 00 00; | load $hex=0
0117 | 10 81 12 00 08 00 00 00; | save modbus $var=m_motion
0118 | 04 01 00 00 00 00 00 00; | exit
0119 | 10 80 0A 00 16 00 00 00; | load $var=workflow
011A | 10 81 12 00 01 00 00 00; | save modbus $var=m_workflow
011B | 04 01 00 00 00 00 00 00; | exit
011C | 03 02 1E 01 10 27 00 00; | reuse #use_send_rcu_relays $sec=1
011D | 04 01 00 00 00 00 00 00; | exit
011E | 02 03 00 00 00 00 00 00; | rcu.read relays
011F | 10 81 12 00 02 00 00 00; | save modbus $var=m_rcu_relays
0120 | 04 01 00 00 00 00 00 00; | exit
0121 | 10 80 01 00 01 00 00 00; | load $dec=1
0122 | 10 81 12 00 03 00 00 00; | save modbus $var=m_master_bed_panel
0123 | 04 01 00 00 00 00 00 00; | exit
0124 | 10 80 01 00 02 00 00 00; | load $dec=2
0125 | 10 81 12 00 03 00 00 00; | save modbus $var=m_master_bed_panel
0126 | 04 01 00 00 00 00 00 00; | exit
0127 | 10 80 01 00 03 00 00 00; | load $dec=3
0128 | 10 81 12 00 03 00 00 00; | save modbus $var=m_master_bed_panel
0129 | 04 01 00 00 00 00 00 00; | exit
012A | 10 80 01 00 04 00 00 00; | load $dec=4
012B | 10 81 12 00 03 00 00 00; | save modbus $var=m_master_bed_panel
012C | 04 01 00 00 00 00 00 00; | exit
012D | 10 80 01 00 01 00 00 00; | load $dec=1
012E | 10 81 12 00 05 00 00 00; | save modbus $var=m_bed1_panel
012F | 04 01 00 00 00 00 00 00; | exit
0130 | 10 80 01 00 02 00 00 00; | load $dec=2
0131 | 10 81 12 00 05 00 00 00; | save modbus $var=m_bed1_panel
0132 | 04 01 00 00 00 00 00 00; | exit
0133 | 10 80 01 00 01 00 00 00; | load $dec=1
0134 | 10 81 12 00 06 00 00 00; | save modbus $var=m_bath1_panel
0135 | 04 01 00 00 00 00 00 00; | exit
0136 | 10 80 01 00 02 00 00 00; | load $dec=2
0137 | 10 81 12 00 06 00 00 00; | save modbus $var=m_bath1_panel
0138 | 04 01 00 00 00 00 00 00; | exit
0139 | 10 80 01 00 03 00 00 00; | load $dec=3
013A | 10 81 12 00 06 00 00 00; | save modbus $var=m_bath1_panel
013B | 04 01 00 00 00 00 00 00; | exit
013C | 10 80 01 00 01 00 00 00; | load $dec=1
013D | 10 81 12 00 04 00 00 00; | save modbus $var=m_entrance_panel
013E | 04 01 00 00 00 00 00 00; | exit
013F | 10 80 01 00 02 00 00 00; | load $dec=2
0140 | 10 81 12 00 04 00 00 00; | save modbus $var=m_entrance_panel
0141 | 04 01 00 00 00 00 00 00; | exit
0142 | 10 80 01 00 03 00 00 00; | load $dec=3
0143 | 10 81 12 00 04 00 00 00; | save modbus $var=m_entrance_panel
0144 | 04 01 00 00 00 00 00 00; | exit
0145 | 10 80 01 00 04 00 00 00; | load $dec=4
0146 | 10 81 12 00 04 00 00 00; | save modbus $var=m_entrance_panel
0147 | 04 01 00 00 00 00 00 00; | exit
0148 | 10 80 01 00 05 00 00 00; | load $dec=5
0149 | 10 81 12 00 04 00 00 00; | save modbus $var=m_entrance_panel
014A | 04 01 00 00 00 00 00 00; | exit
014B | 10 80 01 00 06 00 00 00; | load $dec=6
014C | 10 81 12 00 04 00 00 00; | save modbus $var=m_entrance_panel
014D | 04 01 00 00 00 00 00 00; | exit
014E | 10 80 01 00 01 00 00 00; | load $dec=1
014F | 10 81 12 00 07 00 00 00; | save modbus $var=m_corridor_panel
0150 | 04 01 00 00 00 00 00 00; | exit
0151 | 10 80 01 00 02 00 00 00; | load $dec=2
0152 | 10 81 12 00 07 00 00 00; | save modbus $var=m_corridor_panel
0153 | 04 01 00 00 00 00 00 00; | exit
0154 | 10 80 01 00 03 00 00 00; | load $dec=3
0155 | 10 81 12 00 07 00 00 00; | save modbus $var=m_corridor_panel
0156 | 04 01 00 00 00 00 00 00; | exit
0157 | 10 80 01 00 04 00 00 00; | load $dec=4
0158 | 10 81 12 00 07 00 00 00; | save modbus $var=m_corridor_panel
0159 | 04 01 00 00 00 00 00 00; | exit
015A | 08 01 5E 01 00 00 00 00; | if equal #modbus_user_receive $dec=0
015B | 08 01 61 01 01 00 00 00; | if equal #modbus_workflow_receive $dec=1
015C | 08 01 67 01 02 00 00 00; | if equal #receive_rcu_relays $dec=2
015D | 04 01 00 00 00 00 00 00; | exit
015E | 10 80 12 00 00 00 00 00; | load modbus $var=m_user
015F | 10 81 0A 00 15 00 00 00; | save $var=user
0160 | 04 01 00 00 00 00 00 00; | exit
0161 | 10 80 12 00 01 00 00 00; | load modbus $var=m_workflow
0162 | 10 81 0A 00 16 00 00 00; | save $var=workflow
0163 | 03 02 2A 00 00 00 00 00; | reuse #gsw08_refresh
0164 | 03 02 77 00 00 00 00 00; | reuse #gsw05a_refresh
0165 | 03 02 A7 00 00 00 00 00; | reuse #gsw05b_refresh
0166 | 04 01 00 00 00 00 00 00; | exit
0167 | 10 80 12 00 02 00 00 00; | load modbus $var=m_rcu_relays
0168 | 02 04 00 00 00 00 00 00; | rcu.set all relays from acc
0169 | 04 01 00 00 00 00 00 00; | exit

## Settings3
00 | 02; | 2 | MAC Address | 1 |  |  |  |  | Dir: | C:\tini\ModularHotel\ABSlink\RCUmanager\bin\Release
01 | 01; | 1 |  | 2 |  |  |  |  | Settings page: | 0x0007D000
02 | 36; | 54 |  | 3 |  | 19
03 | 7D; | 125 |  | 4 |  | 109
04 | 6D; | 109 |  | 5 |  | 125
05 | 14; | 19 |  | 6 |  | 54
06 | C0; | 192 | Device IP | 1
07 | A8; | 168 |  | 2
08 | 01; | 1 |  | 3
09 | E0; | 224 |  | 4
0A | FF; | 255 | Mask | 1
0B | FF; | 255 |  | 2
0C | FF; | 255 |  | 3
0D | 00; | 0 |  | 4
0E | 82; | 130 | Gateway | 1
0F | 0A; | 10 |  | 2
10 | 01; | 1 |  | 3
11 | 01; | 1 |  | 4
12 | 10; | 16 | Port | Hi | 4096
13 | 00; | 0 |  | Low
14 | 00; | 0 | Devices/EventMap | 1 |  | Device list followed by event map
15 | C0; | 192 |  | 2 |  | (align 4 byte var/dest)
16 | 07; | 7 |  | 3
17 | 00; | 0 |  | 4
18 | 00; | 0 | AutoStart/Program | 1 |  | Autostart followed by program
19 | 80; | 128 | 0=above 63 blocks 80=standard below 63 blocks | 2 |  | (align 4 byte var/dest)
1A | 07; | 7 |  | 3
1B | 00; | 0 |  | 4
1C | 14; | 20 | DeviceNum | 4 |  | Devices number
1D | 04; | 4 | AutostartNum | Space |  | Number of elements in autoexec
1E | 82; | 130 | TH Server | 1 |  | ModBus pseudoadd FF
1F | 0A; | 10 |  | 2
20 | 01; | 1 |  | 3
21 | DC; | 220 |  | 4
22 | E8; | 232 | Site code | 1
23 | 03; | 3 |  | 2
24 | 00; | 0 |  | 3
25 | 00; | 0 |  | 4
26 | 00; | 0 |  | 5
27 | 00; | 0 |  | 6
28 | 00; | 0 |  | 7
29 | 00; | 0 |  | 8
2A | 81; | 129 | Room number | 1
2B | 00; | 0 |  | 2
2C | 00; | 0 | Building/Extension | 1
2D | 00; | 0 |  | 2
2E | 10; | 16 | TH server port | 1
2F | 00; | 0 |  | 2
30 | 53; | 83 | COM1 | Type |  | Master 115k | Processes sheet
31 | 53; | 83 | COM2 | Type |  | Master 115k
32 | D0; | 83 | COM3 | Type |  | Master 9.6k
33 | 00; | 0 | RF | Type |  | Slave 9600
34 | 01; | 1 | TCP/IP | Type |  | Slave
35 | 14; | 20 | COMTimeout | Par secs |  | Max timeout on answer (in 128 1/10000 secs, 20 =1/4 secs)
36 | 20; | 32 | COM Delay 1 | Tick |  | Delay between packets
37 | 20; | 32 | COM Delay 1 | Tick |  | Delay between packets
38 | 20; | 32 | COM Delay 1 | Tick |  | Delay between packets
39 | 07; | 7 | RCU Relay mask |  |  | security block, filter out thermo relays
3A | 00; | 0 | Thermo1 | Device Num |  | TAG
3B | 00; | 0 | Thermo1 | Type |  | 0=Null, 1=TAG base rel 1/0
3C | 00; | 0 | Thermo1 | Control device |  | 0=RCU, #=device num |  |  |  | 3 | open
3D | 00; | 0 | Thermo1 | Hot relay |  | 0=Null, 1-31 = rel, 32-33 = 0-10V |  |  |  | 4 | close
3E | 00; | 0 | Thermo1 | Cold relay |  | 0=Null, 1-31 = rel, 32-33 = 0-10V
3F | 00; | 0 | Thermo1 | Speed1 relay |  | 0=Null, 1-31 = rel
40 | 00; | 0 | Thermo1 | Speed2 relay |  | 0=Null, 1-31 = rel |  |  |  | 10010011 | 93;
41 | 00; | 0 | Thermo1 | Speed3 relay |  | 0=Null, 1-31 = rel
42 | 00; | 0 | Thermo1 | Window contact |  | 87th bits 00Rcu/01Tag/10Dev, 20h=0NO 1NC, 00hNone, 0fh #Input
43 | 00; | 0 | Thermo2 | Device Num |  | TAG
44 | 00; | 0 | Thermo2 | Type |  | 0=Null, 1=TAG base rel 1/0
45 | 00; | 0 | Thermo2 | Control device |  | 0=RCU, #=device num
46 | 00; | 0 | Thermo2 | Hot relay |  | 0=Null, 1-31 = rel, 32-33 = 0-10V
47 | 00; | 0 | Thermo2 | Cold relay |  | 0=Null, 1-31 = rel, 32-33 = 0-10V
48 | 00; | 0 | Thermo2 | Speed1 relay |  | 0=Null, 1-31 = rel
49 | 00; | 0 | Thermo2 | Speed2 relay |  | 0=Null, 1-31 = rel
4A | 00; | 0 | Thermo2 | Speed3 relay |  | 0=Null, 1-31 = rel
4B | 00; | 0 | Thermo2 | Window contact |  | 87th bits 00Rcu/01Tag/10Dev, 00hNone, #Input number
4C | 00; | 0 | Thermo3 | Device Num |  | TAG
4D | 00; | 0 | Thermo3 | Type |  | 0=Null, 1=TAG base rel 1/0
4E | 00; | 0 | Thermo3 | Control device |  | 0=RCU, #=device num
4F | 00; | 0 | Thermo3 | Hot relay |  | 0=Null, 1-31 = rel, 32-33 = 0-10V
50 | 00; | 0 | Thermo3 | Cold relay |  | 0=Null, 1-31 = rel, 32-33 = 0-10V
51 | 00; | 0 | Thermo3 | Speed1 relay |  | 0=Null, 1-31 = rel
52 | 00; | 0 | Thermo3 | Speed2 relay |  | 0=Null, 1-31 = rel
53 | 00; | 0 | Thermo3 | Speed3 relay |  | 0=Null, 1-31 = rel
54 | 00; | 0 | Thermo3 | Window contact |  | 87th bits 00Rcu/01Tag/10Dev, 00hNone, #Input number
55 | 00; | 0 | Thermo4 | Device Num |  | TAG
56 | 00; | 0 | Thermo4 | Type |  | 0=Null, 1=TAG base rel 1/0
57 | 00; | 0 | Thermo4 | Control device |  | 0=RCU, #=device num
58 | 00; | 0 | Thermo4 | Hot relay |  | 0=Null, 1-31 = rel, 32-33 = 0-10V
59 | 00; | 0 | Thermo4 | Cold relay |  | 0=Null, 1-31 = rel, 32-33 = 0-10V
5A | 00; | 0 | Thermo4 | Speed1 relay |  | 0=Null, 1-31 = rel
5B | 00; | 0 | Thermo4 | Speed2 relay |  | 0=Null, 1-31 = rel
5C | 00; | 0 | Thermo4 | Speed3 relay |  | 0=Null, 1-31 = rel
5D | 00; | 0 | Thermo4 | Window contact |  | 87th bits 00Rcu/01Tag/10Dev, 00hNone, #Input number
5E | 00; | 0 | Thermo5 | Device Num |  | TAG
5F | 00; | 0 | Thermo5 | Type |  | 0=Null, 1=TAG base rel 1/0
60 | 00; | 0 | Thermo5 | Control device |  | 0=RCU, #=device num
61 | 00; | 0 | Thermo5 | Hot relay |  | 0=Null, 1-31 = rel, 32-33 = 0-10V
62 | 00; | 0 | Thermo5 | Cold relay |  | 0=Null, 1-31 = rel, 32-33 = 0-10V
63 | 00; | 0 | Thermo5 | Speed1 relay |  | 0=Null, 1-31 = rel
64 | 00; | 0 | Thermo5 | Speed2 relay |  | 0=Null, 1-31 = rel
65 | 00; | 0 | Thermo5 | Speed3 relay |  | 0=Null, 1-31 = rel
66 | 00; | 0 | Thermo5 | Window contact |  | 87th bits 00Rcu/01Tag/10Dev, 00hNone, #Input number
67 | 00; | 0 | Thermo6 | Device Num |  | TAG
68 | 00; | 0 | Thermo6 | Type |  | 0=Null, 1=TAG base rel 1/0
69 | 00; | 0 | Thermo6 | Control device |  | 0=RCU, #=device num
6A | 00; | 0 | Thermo6 | Hot relay |  | 0=Null, 1-31 = rel, 32-33 = 0-10V
6B | 00; | 0 | Thermo6 | Cold relay |  | 0=Null, 1-31 = rel, 32-33 = 0-10V
6C | 00; | 0 | Thermo6 | Speed1 relay |  | 0=Null, 1-31 = rel
6D | 00; | 0 | Thermo6 | Speed2 relay |  | 0=Null, 1-31 = rel
6E | 00; | 0 | Thermo6 | Speed3 relay |  | 0=Null, 1-31 = rel
6F | 00; | 0 | Thermo6 | Window contact |  | 8th bit 0Rcu/1Tag, 0None, #Input number
70 | 14; | 20 | Thermo* | Speed Ratio |  | FanSpeed=Temperature delta in decimals / ratio
71 | 05; | 5 | Thermo* | Valve Ratio |  | Valve 0-100%= delta temp in cent / ratio
72 | 00; | 0
73 | 00; | 0
74 | 00; | 0 | Thermo* | RunTime Cold | 1 | Running time for the valve in TICK
75 | 00; | 0 | Thermo* | RunTime Cold | 2 | es. 190 sec= 10000*190
76 | 00; | 0 | Thermo* | RunTime Cold | 3 |  | 0 | 00000000
77 | 00; | 0 | Thermo* | RunTime Cold | 4
78 | 00; | 0 | Thermo* | RunTime Hot | 1
79 | 00; | 0 | Thermo* | RunTime Hot | 2
7A | 00; | 0 | Thermo* | RunTime Hot | 3 |  | 0 | 00000000
7B | 00; | 0 | Thermo* | RunTime Hot | 4
7C | 00; | 0
7D | 00; | 0
7E | 00; | 0
7F | 01; | 1
80 | 10; | 16 | Roles opening door | low |  | Permit to define staff open the door
81 | 00; | 0 | Roles opening door | high
82 | 01; | 1 | Ablitate groups opening |  |  | bit1=true
83 | 18; | 24 | Roles blocked by | low |  | HK and HKS
84 | 00; | 0 | flag on event | high
85 | 00; | 0 | RfId mode |  |  | 0=standard, 1=Vingcard mixed
86 | 00; | 0 | RfId data |  |  | On Vingcard mode = starting info for staff
87 | 00; | 0
88 | 01; | 1 | Type of calculation for open valve |  |  | 0=standard, 1=japanese algorithm
89 | 00; | 0
8A | 01; | 1 | Battery if=1 from program, if=0 charging |  |  | bit 0=0 Output on, 1=0 if battery dor lock 100% to-do add new HW
8B | 00; | 0 | Delay on server error |  |  | amount of delay before next send, 0=1 second else (1/10000)<<val
8C | 00; | 0 | FAN remap on valve mode |  |  | 1= fan based on valves according the remap table below
8D | 00; | 0 | Fan1 Fan1 from valve %
8E | 00; | 0 | Fan2 Fan2 from valve %
8F | 00; | 0 | Fan3 Fan3 from valve %
90 | 03; | 3 | BSP1
91 | 00; | 0
92 | 01; | 1
93 | 80; | 128
94 | 00; | 0 | BSP2
95 | 00; | 0
96 | 00; | 0
97 | 00; | 0
98 | 00; | 0 | BSP3
99 | 00; | 0
9A | 00; | 0
9B | 00; | 0
9C | 00; | 0 | BSP4
9D | 00; | 0
9E | 00; | 0
9F | 00; | 0
A0 | 00; | 0 | BSP5
A1 | 00; | 0
A2 | 00; | 0
A3 | 00; | 0
A4 | 00; | 0 | BSP6
A5 | 00; | 0
A6 | 00; | 0
A7 | 00; | 0
A8 | 00; | 0
A9 | 00; | 0
AA | 00; | 0
AB | 00; | 0
AC | 00; | 0
AD | 00; | 0
AE | 00; | 0
AF | 00; | 0
B0 | 00; | 0
B1 | 00; | 0
B2 | 00; | 0
B3 | 00; | 0
B4 | 00; | 0
B5 | 00; | 0
B6 | 00; | 0
B7 | 00; | 0
B8 | 00; | 0
B9 | 00; | 0
BA | 00; | 0
BB | 00; | 0
BC | 00; | 0
BD | 00; | 0
BE | 00; | 0
BF | 00; | 0
C0 | 00; |  | COM4 BusExt |  | !=0 = Activate |  | 3D-5D Kaba - 50 WiFi -10.50.53 ZigBee master 50 vingcard;
C1 | 00; | 1 | COM Ext Type |  | 0, 1=Kaba, 2=WiFi/ZigBee transparent, 3=ZigBeeMaster, 4=WiFiMaster Digi API
C2 | 01; | 1 | Expansio bus type |  | 1=COM, 2=8 relays
C3 | 00; | 0 | Number of locks |  | Address specified on ZigBee addresses from 0x300
C4 | 00; | 0 | ZeroCrossing on Input 8 | 1 | Delay RelayOn/Off on zero crossing (1 activate, >1 delay in TICK)
C5 | 00; | 0 | ZeroCrossing on Input | 2
C6 | 00; | 0 | ZeroCrossing on Input | 3
C7 | 00; | 0 | ZeroCrossing on Input | 4
C8 | 00; | 0 | Offset GMT time -> UTC | 1 | Offset signed INT 32 bit
C9 | 00; | 0 | params set to AUS time | 2 |  | 0 | GMT
CA | 00; | 0 |  | 3 |  | 0 | val
CB | 00; | 0 |  | 4 |  |  | FFFFFFFF-hex(GMT *3600)
CC | 00; | 0
CD | 00; | 0
CE | 00; | 0
CF | 00; | 0
D0 | 00; | 0
D1 | 00; | 0
D2 | 00; | 0
D3 | 00; | 0
D4 | 00; | 0
D5 | 00; | 0
D6 | 00; | 0
D7 | 00; | 0
D8 | 00; | 0
D9 | 00; | 0
DA | 00; | 0
DB | 00; | 0
DC | 00; | 0
DD | 00; | 0
DE | 00; | 0
DF | 00; | 0
E0 | 00; | 0
E1 | 00; | 0
E2 | 00; | 0
E3 | 00; | 0
E4 | 00; | 0
E5 | 00; | 0
E6 | 00; | 0
E7 | 00; | 0
E8 | 00; | 0
E9 | 00; | 0
EA | 00; | 0
EB | 00; | 0
EC | 00; | 0
ED | 00; | 0
EE | 00; | 0
EF | 00; | 0
F0 | 00; | 0
F1 | 00; | 0
F2 | 00; | 0
F3 | 00; | 0
F4 | 00; | 0
F5 | 00; | 0
F6 | 00; | 0
F7 | 00; | 0
F8 | 00; | 0
F9 | 00; | 0
FA | 00; | 0
FB | 00; | 0
FC | 00; | 0
FD | 00; | 0
FE | 00; | 0
FF | 00; | 0
100 | 02; | 2 | Enabled groups |  | 0 |  | Group | 000-007
101 | 00; | 0 |  |  | 1 |  |  | 008-015
102 | 00; | 0 |  |  | 2 |  |  | 016-023
103 | 00; | 0 |  |  | 3
104 | 00; | 0 |  |  | 4
105 | 00; | 0 |  |  | 5
106 | 00; | 0 |  |  | 6
107 | 00; | 0 |  |  | 7
108 | 00; | 0 |  |  | 8
109 | 00; | 0 |  |  | 9
10A | 00; | 0 |  |  | 10
10B | 00; | 0 |  |  | 11
10C | 00; | 0 |  |  | 12
10D | 00; | 0 |  |  | 13
10E | 00; | 0 |  |  | 14
10F | 00; | 0 |  |  | 15
110 | 00; | 0 |  |  | 16
111 | 00; | 0 |  |  | 17
112 | 00; | 0 |  |  | 18
113 | 00; | 0 |  |  | 19
114 | 00; | 0 |  |  | 20
115 | 00; | 0 |  |  | 21
116 | 00; | 0 |  |  | 22
117 | 00; | 0 |  |  | 23
118 | 00; | 0 |  |  | 24
119 | 00; | 0 |  |  | 25
11A | 00; | 0 |  |  | 26
11B | 00; | 0 |  |  | 27
11C | 00; | 0 |  |  | 28
11D | 00; | 0 |  |  | 29
11E | 00; | 0 |  |  | 30
11F | 00; | 0 |  |  | 31 |  |  | 248-255
120 | 00; | 0
121 | 00; | 0
122 | 00; | 0
123 | 00; | 0
124 | 00; | 0
125 | 00; | 0
126 | 00; | 0
127 | 00; | 0
128 | 00; | 0
129 | 00; | 0
12A | 00; | 0
12B | 00; | 0
12C | 00; | 0
12D | 00; | 0
12E | 00; | 0
12F | 00; | 0
130 | 00; | 0
131 | 00; | 0
132 | 00; | 0
133 | 00; | 0
134 | 00; | 0
135 | 00; | 0
136 | 00; | 0
137 | 00; | 0
138 | 00; | 0
139 | 00; | 0
13A | 00; | 0
13B | 00; | 0
13C | 00; | 0
13D | 00; | 0
13E | 00; | 0 |  |  | 30
13F | 00; | 0 |  |  | 31 |  |  | 248-255
140 | 02; | 2 | Enabled groups IDPG2 |  | 0 |  | Group | 000-007
141 | 00; | 0 |  |  | 1 |  |  | 008-015
142 | 00; | 0 |  |  | 2 |  |  | 016-023
143 | 00; | 0 |  |  | 3
144 | 00; | 0 |  |  | 4
145 | 00; | 0 |  |  | 5
146 | 00; | 0 |  |  | 6
147 | 00; | 0 |  |  | 7
148 | 00; | 0 |  |  | 8
149 | 00; | 0 |  |  | 9
14A | 00; | 0 |  |  | 10
14B | 00; | 0 |  |  | 11
14C | 00; | 0 |  |  | 12
14D | 00; | 0 |  |  | 13
14E | 00; | 0 |  |  | 14
14F | 00; | 0 |  |  | 15
150 | 00; | 0 |  |  | 16
151 | 00; | 0 |  |  | 17
152 | 00; | 0 |  |  | 18
153 | 00; | 0 |  |  | 19
154 | 00; | 0 |  |  | 20
155 | 00; | 0 |  |  | 21
156 | 00; | 0 |  |  | 22
157 | 00; | 0 |  |  | 23
158 | 00; | 0 |  |  | 24
159 | 00; | 0 |  |  | 25
15A | 00; | 0 |  |  | 26
15B | 00; | 0 |  |  | 27
15C | 00; | 0 |  |  | 28
15D | 00; | 0 |  |  | 29
15E | 00; | 0 |  |  | 30
15F | 00; | 0 |  |  | 31 |  |  | 248-255
160 | 02; | 2 | Enabled groups IDPG3 |  | 0 |  | Group | 000-007
161 | 00; | 0 |  |  | 1 |  |  | 008-015
162 | 00; | 0 |  |  | 2 |  |  | 016-023
163 | 00; | 0 |  |  | 3
164 | 00; | 0 |  |  | 4
165 | 00; | 0 |  |  | 5
166 | 00; | 0 |  |  | 6
167 | 00; | 0 |  |  | 7
168 | 00; | 0 |  |  | 8
169 | 00; | 0 |  |  | 9
16A | 00; | 0 |  |  | 10
16B | 00; | 0 |  |  | 11
16C | 00; | 0 |  |  | 12
16D | 00; | 0 |  |  | 13
16E | 00; | 0 |  |  | 14
16F | 00; | 0 |  |  | 15
170 | 00; | 0 |  |  | 16
171 | 00; | 0 |  |  | 17
172 | 00; | 0 |  |  | 18
173 | 00; | 0 |  |  | 19
174 | 00; | 0 |  |  | 20
175 | 00; | 0 |  |  | 21
176 | 00; | 0 |  |  | 22
177 | 00; | 0 |  |  | 23
178 | 00; | 0 |  |  | 24
179 | 00; | 0 |  |  | 25
17A | 00; | 0 |  |  | 26
17B | 00; | 0 |  |  | 27
17C | 00; | 0 |  |  | 28
17D | 00; | 0 |  |  | 29
17E | 00; | 0 |  |  | 30
17F | 00; | 0 |  |  | 31 |  |  | 248-255
180 | 02; | 2 | Enabled groups IDPG4 |  | 0 |  | Group | 000-007
181 | 00; | 0 |  |  | 1 |  |  | 008-015
182 | 00; | 0 |  |  | 2 |  |  | 016-023
183 | 00; | 0 |  |  | 3
184 | 00; | 0 |  |  | 4
185 | 00; | 0 |  |  | 5
186 | 00; | 0 |  |  | 6
187 | 00; | 0 |  |  | 7
188 | 00; | 0 |  |  | 8
189 | 00; | 0 |  |  | 9
18A | 00; | 0 |  |  | 10
18B | 00; | 0 |  |  | 11
18C | 00; | 0 |  |  | 12
18D | 00; | 0 |  |  | 13
18E | 00; | 0 |  |  | 14
18F | 00; | 0 |  |  | 15
190 | 00; | 0 |  |  | 16
191 | 00; | 0 |  |  | 17
192 | 00; | 0 |  |  | 18
193 | 00; | 0 |  |  | 19
194 | 00; | 0 |  |  | 20
195 | 00; | 0 |  |  | 21
196 | 00; | 0 |  |  | 22
197 | 00; | 0 |  |  | 23
198 | 00; | 0 |  |  | 24
199 | 00; | 0 |  |  | 25
19A | 00; | 0 |  |  | 26
19B | 00; | 0 |  |  | 27
19C | 00; | 0 |  |  | 28
19D | 00; | 0 |  |  | 29
19E | 00; | 0 |  |  | 30
19F | 00; | 0 |  |  | 31 |  |  | 248-255
1A0 | 02; | 2 | Enabled groups IDPG5 |  | 0 |  | Group | 000-007
1A1 | 00; | 0 |  |  | 1 |  |  | 008-015
1A2 | 00; | 0 |  |  | 2 |  |  | 016-023
1A3 | 00; | 0 |  |  | 3
1A4 | 00; | 0 |  |  | 4
1A5 | 00; | 0 |  |  | 5
1A6 | 00; | 0 |  |  | 6
1A7 | 00; | 0 |  |  | 7
1A8 | 00; | 0 |  |  | 8
1A9 | 00; | 0 |  |  | 9
1AA | 00; | 0 |  |  | 10
1AB | 00; | 0 |  |  | 11
1AC | 00; | 0 |  |  | 12
1AD | 00; | 0 |  |  | 13
1AE | 00; | 0 |  |  | 14
1AF | 00; | 0 |  |  | 15
1B0 | 00; | 0 |  |  | 16
1B1 | 00; | 0 |  |  | 17
1B2 | 00; | 0 |  |  | 18
1B3 | 00; | 0 |  |  | 19
1B4 | 00; | 0 |  |  | 20
1B5 | 00; | 0 |  |  | 21
1B6 | 00; | 0 |  |  | 22
1B7 | 00; | 0 |  |  | 23
1B8 | 00; | 0 |  |  | 24
1B9 | 00; | 0 |  |  | 25
1BA | 00; | 0 |  |  | 26
1BB | 00; | 0 |  |  | 27
1BC | 00; | 0 |  |  | 28
1BD | 00; | 0 |  |  | 29
1BE | 00; | 0 |  |  | 30
1BF | 00; | 0 |  |  | 31 |  |  | 248-255
1C0 | 02; | 2 | Enabled groups IDPG6 |  | 0 |  | Group | 000-007
1C1 | 00; | 0 |  |  | 1 |  |  | 008-015
1C2 | 00; | 0 |  |  | 2 |  |  | 016-023
1C3 | 00; | 0 |  |  | 3
1C4 | 00; | 0 |  |  | 4
1C5 | 00; | 0 |  |  | 5
1C6 | 00; | 0 |  |  | 6
1C7 | 00; | 0 |  |  | 7
1C8 | 00; | 0 |  |  | 8
1C9 | 00; | 0 |  |  | 9
1CA | 00; | 0 |  |  | 10
1CB | 00; | 0 |  |  | 11
1CC | 00; | 0 |  |  | 12
1CD | 00; | 0 |  |  | 13
1CE | 00; | 0 |  |  | 14
1CF | 00; | 0 |  |  | 15
1D0 | 00; | 0 |  |  | 16
1D1 | 00; | 0 |  |  | 17
1D2 | 00; | 0 |  |  | 18
1D3 | 00; | 0 |  |  | 19
1D4 | 00; | 0 |  |  | 20
1D5 | 00; | 0 |  |  | 21
1D6 | 00; | 0 |  |  | 22
1D7 | 00; | 0 |  |  | 23
1D8 | 00; | 0 |  |  | 24
1D9 | 00; | 0 |  |  | 25
1DA | 00; | 0 |  |  | 26
1DB | 00; | 0 |  |  | 27
1DC | 00; | 0 |  |  | 28
1DD | 00; | 0 |  |  | 29
1DE | 00; | 0 |  |  | 30
1DF | 00; | 0 |  |  | 31 |  |  | 248-255
1E0 | 02; | 2 | Enabled groups IDPG7 |  | 0 |  | Group | 000-007
1E1 | 00; | 0 |  |  | 1 |  |  | 008-015
1E2 | 00; | 0 |  |  | 2 |  |  | 016-023
1E3 | 00; | 0 |  |  | 3
1E4 | 00; | 0 |  |  | 4
1E5 | 00; | 0 |  |  | 5
1E6 | 00; | 0 |  |  | 6
1E7 | 00; | 0 |  |  | 7
1E8 | 00; | 0 |  |  | 8
1E9 | 00; | 0 |  |  | 9
1EA | 00; | 0 |  |  | 10
1EB | 00; | 0 |  |  | 11
1EC | 00; | 0 |  |  | 12
1ED | 00; | 0 |  |  | 13
1EE | 00; | 0 |  |  | 14
1EF | 00; | 0 |  |  | 15
1F0 | 00; | 0 |  |  | 16
1F1 | 00; | 0 |  |  | 17
1F2 | 00; | 0 |  |  | 18
1F3 | 00; | 0 |  |  | 19
1F4 | 00; | 0 |  |  | 20
1F5 | 00; | 0 |  |  | 21
1F6 | 00; | 0 |  |  | 22
1F7 | 00; | 0 |  |  | 23
1F8 | 00; | 0 |  |  | 24
1F9 | 00; | 0 |  |  | 25
1FA | 00; | 0 |  |  | 26
1FB | 00; | 0 |  |  | 27
1FC | 00; | 0 |  |  | 28
1FD | 00; | 0 |  |  | 29
1FE | 00; | 0 |  |  | 30
1FF | 00; | 0 |  |  | 31 |  |  | 248-255
200 | 00; | 0
201 | 00; | 0
202 | 00; | 0
203 | 00; | 0
204 | 00; | 0
205 | 00; | 0
206 | 00; | 0
207 | 00; | 0
208 | 00; | 0
209 | 00; | 0
20A | 00; | 0
20B | 00; | 0
20C | 00; | 0
20D | 00; | 0
20E | 00; | 0
20F | 00; | 0
210 | 00; | 0
211 | 00; | 0
212 | 00; | 0
213 | 00; | 0
214 | 00; | 0
215 | 00; | 0
216 | 00; | 0
217 | 00; | 0
218 | 00; | 0
219 | 00; | 0
21A | 00; | 0
21B | 00; | 0
21C | 00; | 0
21D | 00; | 0
21E | 00; | 0
21F | 00; | 0
220 | 00; | 0
221 | 00; | 0
222 | 00; | 0
223 | 00; | 0
224 | 00; | 0
225 | 00; | 0
226 | 00; | 0
227 | 00; | 0
228 | 00; | 0
229 | 00; | 0
22A | 00; | 0
22B | 00; | 0
22C | 00; | 0
22D | 00; | 0
22E | 00; | 0
22F | 00; | 0
230 | 00; | 0
231 | 00; | 0
232 | 00; | 0
233 | 00; | 0
234 | 00; | 0
235 | 00; | 0
236 | 00; | 0
237 | 00; | 0
238 | 00; | 0
239 | 00; | 0
23A | 00; | 0
23B | 00; | 0
23C | 00; | 0
23D | 00; | 0
23E | 00; | 0
23F | 00; | 0
240 | 00; | 0
241 | 00; | 0
242 | 00; | 0
243 | 00; | 0
244 | 00; | 0
245 | 00; | 0
246 | 00; | 0
247 | 00; | 0
248 | 00; | 0
249 | 00; | 0
24A | 00; | 0
24B | 00; | 0
24C | 00; | 0
24D | 00; | 0
24E | 00; | 0
24F | 00; | 0
250 | 00; | 0
251 | 00; | 0
252 | 00; | 0
253 | 00; | 0
254 | 00; | 0
255 | 00; | 0
256 | 00; | 0
257 | 00; | 0
258 | 00; | 0
259 | 00; | 0
25A | 00; | 0
25B | 00; | 0
25C | 00; | 0
25D | 00; | 0
25E | 00; | 0
25F | 00; | 0
260 | 00; | 0
261 | 00; | 0
262 | 00; | 0
263 | 00; | 0
264 | 00; | 0
265 | 00; | 0
266 | 00; | 0
267 | 00; | 0
268 | 00; | 0
269 | 00; | 0
26A | 00; | 0
26B | 00; | 0
26C | 00; | 0
26D | 00; | 0
26E | 00; | 0
26F | 00; | 0
270 | 00; | 0
271 | 00; | 0
272 | 00; | 0
273 | 00; | 0
274 | 00; | 0
275 | 00; | 0
276 | 00; | 0
277 | 00; | 0
278 | 00; | 0
279 | 00; | 0
27A | 00; | 0
27B | 00; | 0
27C | 00; | 0
27D | 00; | 0
27E | 00; | 0
27F | 00; | 0
280 | 00; | 0
281 | 00; | 0
282 | 00; | 0
283 | 00; | 0
284 | 00; | 0
285 | 00; | 0
286 | 00; | 0
287 | 00; | 0
288 | 00; | 0
289 | 00; | 0
28A | 00; | 0
28B | 00; | 0
28C | 00; | 0
28D | 00; | 0
28E | 00; | 0
28F | 00; | 0
290 | 00; | 0
291 | 00; | 0
292 | 00; | 0
293 | 00; | 0
294 | 00; | 0
295 | 00; | 0
296 | 00; | 0
297 | 00; | 0
298 | 00; | 0
299 | 00; | 0
29A | 00; | 0
29B | 00; | 0
29C | 00; | 0
29D | 00; | 0
29E | 00; | 0
29F | 00; | 0
2A0 | 00; | 0
2A1 | 00; | 0
2A2 | 00; | 0
2A3 | 00; | 0
2A4 | 00; | 0
2A5 | 00; | 0
2A6 | 00; | 0
2A7 | 00; | 0
2A8 | 00; | 0
2A9 | 00; | 0
2AA | 00; | 0
2AB | 00; | 0
2AC | 00; | 0
2AD | 00; | 0
2AE | 00; | 0
2AF | 00; | 0
2B0 | 00; | 0
2B1 | 00; | 0
2B2 | 00; | 0
2B3 | 00; | 0
2B4 | 00; | 0
2B5 | 00; | 0
2B6 | 00; | 0
2B7 | 00; | 0
2B8 | 00; | 0
2B9 | 00; | 0
2BA | 00; | 0
2BB | 00; | 0
2BC | 00; | 0
2BD | 00; | 0
2BE | 00; | 0
2BF | 00; | 0
2C0 | 00; | 0
2C1 | 00; | 0
2C2 | 00; | 0
2C3 | 00; | 0
2C4 | 00; | 0
2C5 | 00; | 0
2C6 | 00; | 0
2C7 | 00; | 0
2C8 | 00; | 0
2C9 | 00; | 0
2CA | 00; | 0
2CB | 00; | 0
2CC | 00; | 0
2CD | 00; | 0
2CE | 00; | 0
2CF | 00; | 0
2D0 | 00; | 0
2D1 | 00; | 0
2D2 | 00; | 0
2D3 | 00; | 0
2D4 | 00; | 0
2D5 | 00; | 0
2D6 | 00; | 0
2D7 | 00; | 0
2D8 | 00; | 0
2D9 | 00; | 0
2DA | 00; | 0
2DB | 00; | 0
2DC | 00; | 0
2DD | 00; | 0
2DE | 00; | 0
2DF | 00; | 0
2E0 | 00; | 0
2E1 | 00; | 0
2E2 | 00; | 0
2E3 | 00; | 0
2E4 | 00; | 0
2E5 | 00; | 0
2E6 | 00; | 0
2E7 | 00; | 0
2E8 | 00; | 0
2E9 | 00; | 0
2EA | 00; | 0
2EB | 00; | 0
2EC | 00; | 0
2ED | 00; | 0
2EE | 00; | 0
2EF | 00; | 0
2F0 | 00; | 0
2F1 | 00; | 0
2F2 | 00; | 0
2F3 | 00; | 0
2F4 | 00; | 0
2F5 | 00; | 0
2F6 | 00; | 0
2F7 | 00; | 0
2F8 | 00; | 0
2F9 | 00; | 0
2FA | 00; | 0
2FB | 00; | 0
2FC | 00; | 0
2FD | 00; | 0
2FE | 00; | 0
2FF | 00; | 0
300 | 00; | 0
301 | 00; | 0
302 | 00; | 0
303 | 00; | 0
304 | 00; | 0
305 | 00; | 0
306 | 00; | 0
307 | 00; | 0
308 | 00; | 0
309 | 00; | 0
30A | 00; | 0
30B | 00; | 0
30C | 00; | 0
30D | 00; | 0
30E | 00; | 0
30F | 00; | 0
310 | 00; | 0
311 | 00; | 0
312 | 00; | 0
313 | 00; | 0
314 | 00; | 0
315 | 00; | 0
316 | 00; | 0
317 | 00; | 0
318 | 00; | 0
319 | 00; | 0
31A | 00; | 0
31B | 00; | 0
31C | 00; | 0
31D | 00; | 0
31E | 00; | 0
31F | 00; | 0
320 | 00; | 0
321 | 00; | 0
322 | 00; | 0
323 | 00; | 0
324 | 00; | 0
325 | 00; | 0
326 | 00; | 0
327 | 00; | 0
328 | 00; | 0
329 | 00; | 0
32A | 00; | 0
32B | 00; | 0
32C | 00; | 0
32D | 00; | 0
32E | 00; | 0
32F | 00; | 0
330 | 00; | 0
331 | 00; | 0
332 | 00; | 0
333 | 00; | 0
334 | 00; | 0
335 | 00; | 0
336 | 00; | 0
337 | 00; | 0
338 | 00; | 0
339 | 00; | 0
33A | 00; | 0
33B | 00; | 0
33C | 00; | 0
33D | 00; | 0
33E | 00; | 0
33F | 00; | 0
340 | 00; | 0
341 | 00; | 0
342 | 00; | 0
343 | 00; | 0
344 | 00; | 0
345 | 00; | 0
346 | 00; | 0
347 | 00; | 0
348 | 00; | 0
349 | 00; | 0
34A | 00; | 0
34B | 00; | 0
34C | 00; | 0
34D | 00; | 0
34E | 00; | 0
34F | 00; | 0
350 | 00; | 0
351 | 00; | 0
352 | 00; | 0
353 | 00; | 0
354 | 00; | 0
355 | 00; | 0
356 | 00; | 0
357 | 00; | 0
358 | 00; | 0
359 | 00; | 0
35A | 00; | 0
35B | 00; | 0
35C | 00; | 0
35D | 00; | 0
35E | 00; | 0
35F | 00; | 0
360 | 00; | 0
361 | 00; | 0
362 | 00; | 0
363 | 00; | 0
364 | 00; | 0
365 | 00; | 0
366 | 00; | 0
367 | 00; | 0
368 | 00; | 0
369 | 00; | 0
36A | 00; | 0
36B | 00; | 0
36C | 00; | 0
36D | 00; | 0
36E | 00; | 0
36F | 00; | 0
370 | 00; | 0
371 | 00; | 0
372 | 00; | 0
373 | 00; | 0
374 | 00; | 0
375 | 00; | 0
376 | 00; | 0
377 | 00; | 0
378 | 00; | 0
379 | 00; | 0
37A | 00; | 0
37B | 00; | 0
37C | 00; | 0
37D | 00; | 0
37E | 00; | 0
37F | 00; | 0
380 | 00; | 0
381 | 00; | 0
382 | 00; | 0
383 | 00; | 0
384 | 00; | 0
385 | 00; | 0
386 | 00; | 0
387 | 00; | 0
388 | 00; | 0
389 | 00; | 0
38A | 00; | 0
38B | 00; | 0
38C | 00; | 0
38D | 00; | 0
38E | 00; | 0
38F | 00; | 0
390 | 00; | 0
391 | 00; | 0
392 | 00; | 0
393 | 00; | 0
394 | 00; | 0
395 | 00; | 0
396 | 00; | 0
397 | 00; | 0
398 | 00; | 0
399 | 00; | 0
39A | 00; | 0
39B | 00; | 0
39C | 00; | 0
39D | 00; | 0
39E | 00; | 0
39F | 00; | 0
3A0 | 00; | 0
3A1 | 00; | 0
3A2 | 00; | 0
3A3 | 00; | 0
3A4 | 00; | 0
3A5 | 00; | 0
3A6 | 00; | 0
3A7 | 00; | 0
3A8 | 00; | 0
3A9 | 00; | 0
3AA | 00; | 0
3AB | 00; | 0
3AC | 00; | 0
3AD | 00; | 0
3AE | 00; | 0
3AF | 00; | 0
3B0 | 00; | 0
3B1 | 00; | 0
3B2 | 00; | 0
3B3 | 00; | 0
3B4 | 00; | 0
3B5 | 00; | 0
3B6 | 00; | 0
3B7 | 00; | 0
3B8 | 00; | 0
3B9 | 00; | 0
3BA | 00; | 0
3BB | 00; | 0
3BC | 00; | 0
3BD | 00; | 0
3BE | 00; | 0
3BF | 00; | 0
3C0 | 00; | 0
3C1 | 00; | 0
3C2 | 00; | 0
3C3 | 00; | 0
3C4 | 00; | 0
3C5 | 00; | 0
3C6 | 00; | 0
3C7 | 00; | 0
3C8 | 00; | 0
3C9 | 00; | 0
3CA | 00; | 0
3CB | 00; | 0
3CC | 00; | 0
3CD | 00; | 0
3CE | 00; | 0
3CF | 00; | 0
3D0 | 00; | 0
3D1 | 00; | 0
3D2 | 00; | 0
3D3 | 00; | 0
3D4 | 00; | 0
3D5 | 00; | 0
3D6 | 00; | 0
3D7 | 00; | 0
3D8 | 00; | 0
3D9 | 00; | 0
3DA | 00; | 0
3DB | 00; | 0
3DC | 00; | 0
3DD | 00; | 0
3DE | 00; | 0
3DF | 00; | 0
3E0 | 00; | 0
3E1 | 00; | 0
3E2 | 00; | 0
3E3 | 00; | 0
3E4 | 00; | 0
3E5 | 00; | 0
3E6 | 00; | 0
3E7 | 00; | 0
3E8 | 00; | 0
3E9 | 00; | 0
3EA | 00; | 0
3EB | 00; | 0
3EC | 00; | 0
3ED | 00; | 0
3EE | 00; | 0
3EF | 00; | 0
3F0 | 00; | 0
3F1 | 00; | 0
3F2 | 00; | 0
3F3 | 00; | 0
3F4 | 00; | 0
3F5 | 00; | 0
3F6 | 00; | 0
3F7 | 00; | 0
3F8 | 00; | 0
3F9 | 00; | 0
3FA | 00; | 0
3FB | 00; | 0
3FC | 00; | 0
3FD | 00; | 0
3FE | 00; | 0
3FF | 00; | 0
400 | 00; | 0
401 | 00; | 0
402 | 00; | 0
403 | 00; | 0
404 | 00; | 0
405 | 00; | 0
406 | 00; | 0
407 | 00; | 0
408 | 00; | 0
409 | 00; | 0
40A | 00; | 0
40B | 00; | 0
40C | 00; | 0
40D | 00; | 0
40E | 00; | 0
40F | 00; | 0
410 | 00; | 0
411 | 00; | 0
412 | 00; | 0
413 | 00; | 0
414 | 00; | 0
415 | 00; | 0
416 | 00; | 0
417 | 00; | 0
418 | 00; | 0
419 | 00; | 0
41A | 00; | 0
41B | 00; | 0
41C | 00; | 0
41D | 00; | 0
41E | 00; | 0
41F | 00; | 0
420 | 00; | 0

## CustomVar3
Variable short name | Description for variable
80 | last_action
82 | pir
85 | user_backup
86 | C/F

## ModbusVar3
Variable short name | Description for variable
0 | m_user
1 | m_workflow
2 | m_rcu_relays
3 | m_master_bed_panel
4 | m_entrance_panel
5 | m_bed1_panel
6 | m_bath1_panel
7 | m_corridor_panel
8 | m_motion
9 | m_notify | 0=restart 1=panelpress

## Device4
| ;Devices.hex | [9 empty] | Event map |  |  | Dir: | C:\tini\ModularHotel\ABSlink\RCUmanager\bin\Release
| ;Enum | Type | Id | COM | Pt Event map |  |  |  | lo hi |  | 16bit pt to program |  |  | 0000=none |  |  |  | Enum/Priority
| ;/Priority |  |  |  | lo hi |  | EnumHex | Enum | Progran |  | Start with RCU event |  |  | 8000=activate standard management |  |  |  | Enum is used in multi devices to manage variable offseting
1 | 00 | 00 | 00 | 00 | 00 00 | ; | 00 | 0 | 00 00; | RCU | Startup |  |  | 4000=only on guest presence
2 | 00 | 00 | 00 | 00 | 00 00 | ; | 01 | 1 | 00 00; |  | Watchdog |  |  | bit 15 permit to flag both (standard+program)
3 | 01 | 03 | 1E | 01 | 21 00 | ;TAG1 | 02 | 2 | 00 00; |  | Battery | start |  | bit 14 only guest action
4 | 00 | 00 | 00 | 00 | 00 00 | ; | 03 | 3 | 00 00; |  | Battery | end
5 | 00 | 00 | 00 | 00 | 00 00 | ; | 04 | 4 | 00 00; |  | Battery | low |  | Types
6 | 00 | 00 | 00 | 00 | 00 00 | ; | 05 | 5 | 00 00; |  | Input | 1 on |  | 1 | IDPG
7 | 00 | 00 | 00 | 00 | 00 00 | ; | 06 | 6 | 00 00; |  | Input | 1 off |  | 2 | TIG
8 | 00 | 00 | 00 | 00 | 00 00 | ; | 07 | 7 | 00 00; |  | Input | 2 on |  | 3 | TAG
9 | 00 | 00 | 00 | 00 | 00 00 | ; | 08 | 8 | 00 00; |  | Input | 2 off |  | 4 | IOEXP
10 | 00 | 00 | 00 | 00 | 00 00 | ; | 09 | 9 | 00 00; |  | Input | 3 on |  | 5 | IODEXP
11 | 01 | 0C | 80 | 02 | 33 00 | ;Temp-hub7 | 0A | 10 | 00 00; |  | Input | 3 off |  | 6 | GSW |  | IOEXP with polling on Input
12 | 00 | 00 | 00 | 00 | 00 00 | ; | 0B | 11 | 00 00; |  | Input | 4 on |  | 7 | IOEXPIN
13 | 00 | 00 | 00 | 00 | 00 00 | ; | 0C | 12 | 00 00; |  | Input | 4 off |  | 8 | BSP RF
14 | 00 | 00 | 00 | 00 | 00 00 | ; | 0D | 13 | 00 00; |  | Input | 5 on |  | 9 | BSP wired
15 | 00 | 00 | 00 | 00 | 00 00 | ; | 0E | 14 | 00 00; |  | Input | 5 off |  | 128 | General Modbus
16 | 00 | 00 | 00 | 00 | 00 00 | ; | 0F | 15 | 00 00; |  | Input | 6 on |  | 129 | General IP |  | Id+Com=Port Pt=last 2 IP addr
17 | 00 | 00 | 00 | 00 | 00 00 | ; | 10 | 16 | 00 00; |  | Input | 6 off
18 | 00 | 00 | 00 | 00 | 00 00 | ; | 11 | 17 | 00 00; |  | Input | 7 on |  | Id | FF | Server
19 | 00 | 00 | 00 | 00 | 00 00 | ; | 12 | 18 | 00 00; |  | Input | 7 off |  |  | FE | Calling device
20 | 00 | 00 | 00 | 00 | 00 00 | ; | 13 | 19 | 00 00; |  | Input | 8 on
[7 empty] | 14 | 20 | 00 00; |  | Input | 8 off
[7 empty] | 15 | 21 | 00 00; |  | Thermo | on
[7 empty] | 16 | 22 | 7F 00; |  | Evt grp write (reg) |  | modbus_manager
[7 empty] | 17 | 23 | 00 00; |  | Evt grp write (reg)
[7 empty] | 18 | 24 | 00 00; |  | MUR | off
[7 empty] | 19 | 25 | 00 00; |  | SOS | on
[7 empty] | 1A | 26 | 00 00; |  | SOS | off
[7 empty] | 1B | 27 | 00 00; |  | Laundry | on
[7 empty] | 1C | 28 | 00 00; |  | Laundry | off
[7 empty] | 1D | 29 | 00 00; |  | Call | on
[7 empty] | 1E | 30 | 00 00; |  | Call | off
[7 empty] | 1F | 31 | 00 00; |  | Card Ok
[7 empty] | 20 | 32 | 00 00; |  | Card Nok
[7 empty] | 21 | 33 | 00 00; | TAG1 | OffLine
[7 empty] | 22 | 34 | 00 00; |  | C/F
[7 empty] | 23 | 35 | 00 00;
[7 empty] | 24 | 36 | 00 00; |  | out temp
[7 empty] | 25 | 37 | 6A 40; |  | Btn - |  | tag1_readsetpoint
[7 empty] | 26 | 38 | 6A 40; |  | Btn + |  | tag1_readsetpoint
[7 empty] | 27 | 39 | 4B 40; |  | Fan1 |  | tag1_fan1
[7 empty] | 28 | 40 | 4F 40; |  | Fan2 |  | tag1_fan2
[7 empty] | 29 | 41 | 53 40; |  | Fan3 |  | tag1_fan3
[7 empty] | 2A | 42 | 57 40; |  | Auto |  | tag1_auto
[7 empty] | 2B | 43 | 5B 40; |  | Eco |  | tag1_eco
[7 empty] | 2C | 44 | 5F 40; |  | Off |  | tag1_off
[7 empty] | 2D | 45 | 00 00; |  | Input 1 on
[7 empty] | 2E | 46 | 00 00; |  | Input 1 off
[7 empty] | 2F | 47 | 00 00; |  | Input 2 on
[7 empty] | 30 | 48 | 00 00; |  | Input 2 off
[7 empty] | 31 | 49 | 00 00; |  | Dummy
[7 empty] | 32 | 50 | 70 00; |  | Press no right |  | tag1_resetsetpoint
[7 empty] | 33 | 51 | 00 00; | Temp-Hub1 | OffLine

## XCODE4
XCODE [0.9,2]
0 | #startup
1 | version [35561452341814213551145390817034,9]
2 | goto #debugging
3 | reserved for ipad
4 | reserved for ipad
5 | reserved for ipad
6 | reserved for ipad
7 | reserved for ipad
8 | reserved for ipad
9 | reserved for ipad
10 | reserved for ipad
11 | reserved for ipad
12 | reserved for ipad
13 | reserved for ipad
14 | reserved for ipad
15 | reserved for ipad
16 | reserved for ipad
17 | reserved for ipad
18 | reserved for ipad
19 | reserved for ipad
20 | reserved for ipad
21 | reserved for ipad
22 | reserved for ipad
23 | goto #checkout
24 | goto #checkin
25
26 | function startup
27 | //send.modbus $dev=server $reg=0 $dec=0
28 | send.modbus $type=tag $reg=15 $dec=50*10 //button interactive
29 | send.modbus $type=tag $reg=16 $dec=5*10 //button non-interactive
30 | send.modbus $type=tag $reg=17 $dec=80*10 //display interactive
31 | send.modbus $type=tag $reg=18 $dec=5*10 //display non-interactive
32 | send.modbus $type=gsw $reg=15 $dec=80*10
33 | send.modbus $type=gsw $reg=16 $dec=30*10
34 | run #tag_flash $sec=15
35 | reuse #tag1_current_temp $sec=20
36 | reuse #temp_probe_cycle $min=1
37 | wait $sec=5
38 | m_notify.set $dec=0
39 | exit
40
41
42 | function debugging
43 | debug
44 | exit
45
46
47 | //function gsw_motion_settings
48 | //send.modbus $dev=gsw1 $reg=80 $hex=63
49 | //send.modbus $dev=gsw1 $reg=81 $hex=15E
50 | //send.modbus $dev=gsw1 $reg=82 $hex=02
51 | //exit
52
53
54 | //function thermo_cycle
55 | //send.modbus $dev=server $reg=14 $len=16
56 | //exit
57
58 | //function dev_offline
59 | //send.modbus $dev=server $reg=8 $len=4
60 | //exit
61
62
63 | function checkout
64 | exit
65
66
67
68 | function checkin
69 | goto #checkout
70 | exit
71
72
73
74
75 | function tag_flash
76 | load $var=tag_minmax
77 | if not equal #+3 $hex=0
78 | tag_minmax.set $dec=19*256+28
79 | send.modbus $type=tag $reg=6 $len=2
80 | //load $dec=24*10
81 | //save $var=temp1
82 | //send.modbus $type=tag $reg=25 $len=2
83 | //load $fan=fan1
84 | //save $var=thermo1
85 | reuse #min_fan_speed_check
86 | //room_empty.set $hex=8014
87 | anti_ice.set $dec=65536*35*10+5*10
88 | intervention.set $dec=65536*0.5*10+0.1*10
89 | send.modbus $type=tag $reg=3 $dec=2 //disable top buttons
90 | wait $sec=0.01
91 | send.modbus $type=tag $reg=8 $hex=2 //TAGs +/- steps 0.5 degrees
92 | load $var=user
93 | if not equal #refresh_tag1 $hex=0
94 | load $hex=80
95 | send.modbus $type=tag $reg=13 $len=4
96 | exit
97
98
99
100 | function min_fan_speed_check
101 | load $var=user
102 | if bit true #+4 $hex=ff
103 | season.set $hex=01 //summer - min fan speed
104 | exit
105 | season.set $hex=11 //summer + min fan speed
106 | exit
107
108
109
110
111 | function refresh_tag1
112 | load $var=thermo1
113 | math.and $hex=aaaa
114 | if equal #+2 $hex=80
115 | math.shiftR $dec=1
116 | send.modbus $dev=tag1 $reg=13 $len=4
117 | exit
118
119 | function tag1_fan1
120 | //send.modbus $dev=server $reg=13 $hex=0001
121 | load $hex=0601
122 | save modbus $var=m_fcu_speed
123 | load $fan=fan1
124 | goto #tag1_common
125
126 | function tag1_fan2
127 | //send.modbus $dev=server $reg=13 $hex=0002
128 | load $hex=0602
129 | save modbus $var=m_fcu_speed
130 | load $fan=fan2
131 | goto #tag1_common
132
133 | function tag1_fan3
134 | //send.modbus $dev=server $reg=13 $hex=0003
135 | load $hex=0603
136 | save modbus $var=m_fcu_speed
137 | load $fan=fan3
138 | goto #tag1_common
139
140 | function tag1_auto
141 | //send.modbus $dev=server $reg=13 $hex=0004
142 | load $hex=0604
143 | save modbus $var=m_fcu_speed
144 | load $fan=auto
145 | goto #tag1_common
146
147 | function tag1_eco
148 | //send.modbus $dev=server $reg=13 $hex=0005
149 | load $hex=0605
150 | save modbus $var=m_fcu_speed
151 | load $fan=eco
152 | goto #tag1_common
153
154 | function tag1_off
155 | //send.modbus $dev=server $reg=13 $hex=0006
156 | load $hex=0606
157 | save modbus $var=m_fcu_speed
158 | load $fan=off
159 | function tag1_common
160 | save $var=thermo1
161 | send.modbus $dev=tag1 $reg=13 $len=4
162 | reuse #refresh_tag1 $sec=15
163 | exit
164
165 | function tag1_wakeup
166 | load $var=thermo1
167 | send.modbus $dev=tag1 $reg=13 $len=4
168 | reuse #refresh_tag1 $sec=15
169 | exit
170
171 | function tag1_readsetpoint
172 | reuse #tag1_wakeup
173 | wait $sec=6
174 | read.modbus $dev=tag1 $reg=25
175 | save $var=temp1
176 | save modbus $var=m_fcu_setpoint
177 | //load shift enum
178 | //send.modbus $dev=server $reg=11 $len=8
179 | exit
180
181 | function tag1_resetsetpoint
182 | wait $sec=2
183 | load $var=room_empty
184 | if less than #+3 $hex=8000
185 | math.and $relay=16
186 | math.add $var=temp1
187 | send.modbus $dev=tag1 $reg=25 $len=2
188 | exit
189
190
191
192
193 | function tag1_current_temp
194 | read.modbus $dev=tag1 $reg=9
195 | save modbus $var=m_current_temp
196 | goto #tag1_current_temp $min=10
197
198
199
200
201
202
203
204 | function send_rcu_relays
205 | reuse #use_send_rcu_relays $sec=1
206 | exit
207 | function use_send_rcu_relays
208 | rcu.read relays
209 | save modbus $var=m_rcu_relays
210 | exit
211
212
213
214
215
216
217
218 | //receive modbus
219
220
221 | function modbus_manager
222 | if equal #modbus_user_receive $dec=0
223 | if equal #modbus_workflow_receive $dec=1
224 | if equal #modbus_receive_rcu_relays $dec=2
225 | if equal #modbus_receive_tag_fan $dec=4
226 | if equal #modbus_receive_tag_temp $dec=5
227 | if equal #modbus_receive_bell $dec=6
228 | exit
229
230
231 | function modbus_user_receive
232 | load modbus $var=m_user
233 | save $var=user
234 | if equal #tag_without_user $hex=0
235 | load $var=temp1
236 | send.modbus $type=tag $reg=25 $len=2
237 | reuse #refresh_tag1 $dev=tag1
238 | season.set $hex=11 //summer + min fan speed
239 | exit
240 | function tag_without_user
241 | reuse #refresh_tag1 $dev=tag1
242 | load $var=room_empty
243 | if less than #+3 $hex=8000
244 | math.and $relay=16
245 | math.add $var=temp1
246 | send.modbus $dev=tag1 $reg=25 $len=2
247 | season.set $hex=01 //summer - min fan speed
248 | wait $sec=2
249 | load $hex=80
250 | send.modbus $dev=tag1 $reg=13 $len=4
251 | exit
252
253
254 | function modbus_workflow_receive
255 | load modbus $var=m_workflow
256 | save $var=workflow
257 | exit
258
259
260
261 | function modbus_receive_rcu_relays
262 | load modbus $var=m_rcu_relays
263 | math.and $relay=1-3,8 //fcu and bell
264 | save $var=fcu_filter
265 | rcu.read relays
266 | math.and.or $relay=4-32 $var=fcu_filter
267 | rcu.set all relays from acc
268 | exit
269
270
271
272 | function modbus_receive_tag_fan
273 | load modbus $var=m_fcu_speed
274 | math.or $hex=3f0000
275 | save $var=thermo1
276 | reuse #refresh_tag1 $dev=tag1
277 | exit
278
279
280
281 | function modbus_receive_tag_temp
282 | load modbus $var=m_fcu_setpoint
283 | save $var=temp1
284 | send.modbus $dev=tag1 $reg=25 $len=2
285 | exit
286
287
288
289 | function modbus_receive_bell
290 | load modbus $var=m_bell_ring
291 | if not equal #exit $hex=1
292 | rcu.set $relay=8
293 | wait $sec=0.18
294 | rcu.unset $relay=8
295 | exit
296
297
298
299 | function temp_probe_cycle
300 | //7th hub
301 | read.modbus $dev=11 $reg=3
302 | if equal goto #+3 $var=PT100_7_water_return
303 | save $var=PT100_7_water_return
304 | save modbus $var=m_PT100_7_water_return
305 | wait $sec=30
306 | read.modbus $dev=11 $reg=4
307 | if equal goto #+3 $var=PT100_7_water_supply
308 | save $var=PT100_7_water_supply
309 | save modbus $var=m_PT100_7_water_supply
310 | wait $sec=30
311 | read.modbus $dev=11 $reg=5
312 | if equal goto #+3 $var=PT100_7_air_return
313 | save $var=PT100_7_air_return
314 | save modbus $var=m_PT100_7_air_return
315 | wait $sec=30
316 | read.modbus $dev=11 $reg=6
317 | if equal goto #+3 $var=PT100_7_air_supply
318 | save $var=PT100_7_air_supply
319 | save modbus $var=m_PT100_7_air_supply
320 | goto #temp_probe_cycle $min=3
321
322
323
324
325
326

## Program4
| ; |  | Dir: | C:\tini\ModularHotel\ABSlink\RCUmanager\bin\Release
| ;code |  | # | Description | done | Parameters (8 bytes)
0000 | 19 00 00 00 00 00 00 00; | #startup | 0x01 | GoTo & Wait | d | 0x01 | wait # tick |  | 2bytete optional goto |  |  | tick | [5 empty] | 00=nogoto 00=nowait
0001 | 00 00 00 00 09 2E ED 09; | version [35561452341814213551145390817034,9] |  |  | d | 0x03 | WaitTick/OrigDev |  | 2byte goto (acc->acc called) |  |  | tick | Relative, reuse of existing task with same device if present updating tick (used for timeout interactive mode) [multidev]
0002 | 01 01 26 00 00 00 00 00; | goto #debugging | 0x0a | Wait absolute | d | 1=value,3=1B,4=2B, 5=4B,a=acc[0]=RTC(add), |  |  |  |  | 2 byte empty |  |  |  | 4 byte value |  | 3-5= addr a-b uses RTC+acc[0]
0003 | 01 01 00 00 00 00 00 00; | reserved for ipad | 0x02 | Rcu Hardware | d | 0x01 | set relay |  | 0=accum, 1=value, 3=add1B, 4=add2B, 5=add4B | [5 empty] | byte low bitmap from relay 1 to 8
0004 | 01 01 00 00 00 00 00 00; | reserved for ipad |  |  | d | 0x02 | unset relay |  | 0=accum, 1=value, 3=add1B, 4=add2B, 5=add4B | [5 empty] | byte low bitmap from relay 1 to 8
0005 | 01 01 00 00 00 00 00 00; | reserved for ipad |  |  | d | 0x03 | read relays in accumulator
0006 | 01 01 00 00 00 00 00 00; | reserved for ipad |  |  | d | 0x04 | set all relays |  | 0=accum, 1=value, 3=add1B, 4=add2B, 5=add4B | [5 empty] | bitmap
0007 | 01 01 00 00 00 00 00 00; | reserved for ipad |  |  | d | 0x05 | set OUT Lock % |  | 0=accum, 1=value, 3=add1B, 4=add2B, 5=add4B | [5 empty] | 50% = 12Volt
0008 | 01 01 00 00 00 00 00 00; | reserved for ipad |  |  | d | 0x06 | set 0-10 V [1] |  | 0=accum, 1=value, 3=add1B, 4=add2B, 5=add4B
0009 | 01 01 00 00 00 00 00 00; | reserved for ipad |  |  | d | 0x07 | set 0-10 V [2] |  | 0=accum, 1=value, 3=add1B, 4=add2B, 5=add4B
000A | 01 01 00 00 00 00 00 00; | reserved for ipad |  |  |  | 0x08 | Input->Accumulator |  | Input # |  |  | Get inputs value in accumulator, if par1=0 all inputs (bitmap)
000B | 01 01 00 00 00 00 00 00; | reserved for ipad |  |  | d | 0x09 | set on relays |  | 0=accum, 1=value, 3=add1B, 4=add2B, 5=add4B | [5 empty] | bitmap
000C | 01 01 00 00 00 00 00 00; | reserved for ipad |  |  | d | 0x0a | set off relays |  | 0=accum, 1=value, 3=add1B, 4=add2B, 5=add4B | [5 empty] | bitmap
000D | 01 01 00 00 00 00 00 00; | reserved for ipad |  |  | d | 0x0b | xor relays |  | 0=accum, 1=value, 3=add1B, 4=add2B, 5=add4B | [5 empty] | bitmap
000E | 01 01 00 00 00 00 00 00; | reserved for ipad | 0x03 | Run task | d | 0x01 | NewTask Wait # tick |  | 2byte goto |  |  | tick | Run a separate thread
000F | 01 01 00 00 00 00 00 00; | reserved for ipad |  |  | d | 0x02 | Reuse Wait # tick |  | 2byte goto (acc->acc called) |  |  | tick | Relative, reuse of existing task if present updating tick (used for timeout interactive mode)
0010 | 01 01 00 00 00 00 00 00; | reserved for ipad |  |  | d | 0x03 | Reuse/WaitTick/OrigDev |  | 2byte goto (acc->acc called) |  |  | tick | Relative, reuse of existing task with same device if present updating tick (used for timeout interactive mode) [multidev]
0011 | 01 01 00 00 00 00 00 00; | reserved for ipad | 0x04 | Exit | d | 0x01 | Stop execution
0012 | 01 01 00 00 00 00 00 00; | reserved for ipad |  |  |  | 0x02 | Return to caller in accumulator
0013 | 01 01 00 00 00 00 00 00; | reserved for ipad | 0x05 | GoTo if acc[0] != | d |  | 0=acc, 1=value, 3=addr 1B, 4=addr 2B, 5=addr 4B | [6 empty] | 2byte goto |  | 4bytes value
0014 | 01 01 00 00 00 00 00 00; | reserved for ipad | 0x06 | GoTo if acc[0] > | d |  | 0=acc, 1=value, 3=addr 1B, 4=addr 2B, 5=addr 4B | [6 empty] | 2byte goto |  | 4bytes value
0015 | 01 01 00 00 00 00 00 00; | reserved for ipad | 0x07 | GoTo if acc[0] < | d |  | 0=acc, 1=value, 3=addr 1B, 4=addr 2B, 5=addr 4B | [6 empty] | 2byte goto |  | 4bytes value
0016 | 01 01 00 00 00 00 00 00; | reserved for ipad | 0x08 | GoTo if acc[0] = | d |  | 0=acc, 1=value, 3=addr 1B, 4=addr 2B, 5=addr 4B | [6 empty] | 2byte goto |  | 4bytes value
0017 | 01 01 28 00 00 00 00 00; | goto #checkout | 0x09 | GoTo if acc[0] AND | d |  | 0=acc, 1=value, 3=addr 1B, 4=addr 2B, 5=addr 4B | [6 empty] | 2byte goto |  | 4bytes value |  |  | goto if a bit match
0018 | 01 01 29 00 00 00 00 00; | goto #checkin | 0x10 | Mathematics | d | 0x01 | Add | 1=value, 2=RPN, 3=addr 1B, 4=addr 2B, 5=addr 4B | [5 empty] | empty | 4 byte value |  | 1 value is from last 4 bytes
0019 | 21 03 00 0F 01 F4 00 00; | send.modbus $type=tag $reg=15 $dec=50*10 |  |  | d | 0x02 | Sub | 1=value, 2=RPN, 3=addr 1B, 4=addr 2B, 5=addr 4B | [5 empty] | empty | 4 byte value |  | 2 RPN operates in Accumulator and last stack, shift down 3 values in stack
001A | 21 03 00 10 00 32 00 00; | send.modbus $type=tag $reg=16 $dec=5*10 |  |  | d | 0x03 | Mul | 1=value, 2=RPN, 3=addr 1B, 4=addr 2B, 5=addr 4B | [5 empty] | empty | 4 byte value |  | 3-5 uses memory with 1,2,4 bytes
001B | 21 03 00 11 03 20 00 00; | send.modbus $type=tag $reg=17 $dec=80*10 |  |  | d | 0x04 | OR | 1=value, 2=RPN, 3=addr 1B, 4=addr 2B, 5=addr 4B | [5 empty] | empty | 4 byte value
001C | 21 03 00 12 00 32 00 00; | send.modbus $type=tag $reg=18 $dec=5*10 |  |  | d | 0x05 | XOR | 1=value, 2=RPN, 3=addr 1B, 4=addr 2B, 5=addr 4B | [5 empty] | empty | 4 byte value |  | Stack is 3 values + Accumulator like Forth
001D | 21 06 00 0F 03 20 00 00; | send.modbus $type=gsw $reg=15 $dec=80*10 |  |  | d | 0x06 | AND | 1=value, 2=RPN, 3=addr 1B, 4=addr 2B, 5=addr 4B | [5 empty] | empty | 4 byte value
001E | 21 06 00 10 01 2C 00 00; | send.modbus $type=gsw $reg=16 $dec=30*10 |  |  | d | 0x07 | << | 1=value, 2=RPN, 3=addr 1B, 4=addr 2B, 5=addr 4B | [5 empty] | empty | 4 byte value
001F | 03 01 2B 00 F0 49 02 00; | run #tag_flash $sec=15 |  |  | d | 0x08 | >> | 1=value, 2=RPN, 3=addr 1B, 4=addr 2B, 5=addr 4B | [5 empty] | empty | 4 byte value |  |  | 1B=byte, 2B=16bit, 4B=32bit
0020 | 03 02 77 00 40 0D 03 00; | reuse #tag1_current_temp $sec=20 |  |  | d | 0x09 | Div | 0=Acc, 1=value, 2=RPN, 3=addr 1B, 4=addr 2B, 5=addr 4B | [5 empty] | empty | 4 byte value |  | 3-5 uses memory with 1,2,4 bytes
0021 | 03 02 B5 00 C0 27 09 00; | reuse #temp_probe_cycle $min=1 |  |  | d | 0x0a | Mod | 0=Acc, 1=value, 2=RPN, 3=addr 1B, 4=addr 2B, 5=addr 4B | [5 empty] | empty | 4 byte value |  | 3-5 uses memory with 1,2,4 bytes
0022 | 01 01 00 00 50 C3 00 00; | wait $sec=5 |  |  | d | 0x80 | PUSH | 1=value,3=1B,4=2B, 5=4B,a=acc[0]=RTC(add), | [5 empty] | shiftYN | 4 byte value |  | 3-5= addr a-b uses RTC+acc[0]
0023 | 10 80 01 00 00 00 00 00; | load $dec=0 |  |  | d | [8 empty] | shiftYN | 1 item size |  | 1 byte relative positive address, 1 elements, 1 empty
0024 | 10 81 12 00 0B 00 00 00; | save modbus $var=m_notify |  |  | d | [8 empty] | shiftYN | 1 item size |  | 1 byte relative positive address, 1 elements, 1 empty
0025 | 04 01 00 00 00 00 00 00; | exit |  |  | d |  |  | e=CurrentEventDevice, f=addr 4B+OrigDevEnum(DeviceMap) | [5 empty] | shiftYN | 4 byte value
0026 | 40 01 01 00 00 00 00 00; | debug |  |  | d | 0x81 | POP | 3=1B,4=2B,5=4B,a=RTC(add)=acc[0],b=RTC(acc[0])=acc[1] | [5 empty] | shiftYN | 4 byte value
0027 | 04 01 00 00 00 00 00 00; | exit |  |  | d |  |  | e=CurrentEventDevice, f=addr 4B+OrigDevEnum(DeviceMap) | [5 empty] | shiftYN | 4 byte value
0028 | 04 01 00 00 00 00 00 00; | exit |  |  | d | 0x82 | PUSH time | [6 empty] | shiftYN
0029 | 01 01 28 00 00 00 00 00; | goto #checkout | 0x20 | Send ModBus 1 Word | d | Dest | PosHi | PosLo | Whi | Wlo | crcH | crcL |  | Dest FF=ServerIP, FE=OrigDevice |  |  |  |  | # dev map (Type=all devices with specified type)
002A | 04 01 00 00 00 00 00 00; | exit | 0x21 | Send ModBus 1 Word | d | Type | PosHi | PosLo | Whi | Wlo | crcH | crcL |  | Dest FF=ServerIP, FE=OrigDevice |  |  |  |  | Send to all devices with type=x
002B | 10 80 0A 00 27 00 00 00; | load $var=tag_minmax | 0x22 | Send ModBus Accumulator | d | Dest | PosHi | PosLo | bytes(2-16),NW |  | crcH | crcL |  | Dest FF=ServerIP, FE=OrigDevice |  |  |  |  | NW=no wait
002C | 05 01 2F 00 00 00 00 00; | if not equal #+3 $hex=0 | 0x23 | Send ModBus Accumulator | d | Type | PosHi | PosLo | bytes(2-16),00 |  | crcH | crcL |  | Dest FF=ServerIP, FE=OrigDevice |  |  |  |  | Send to all devices with type=x
002D | 10 80 01 00 1C 13 00 00; | load $dec=19*256+28 | 0x26 | Read modbus in Accumulator | d | Dest | PosHi | PosLo | bytes(2,4), 00 |  | crcH | crcL |  | Dest FF=ServerIP, FE=OrigDevice
002E | 10 81 0A 00 27 00 00 00; | save $var=tag_minmax | 0x2a | Seand modbus Acc[*] | d d d: d; PUSH time Whi Whi: Dest+PosH+PosL+Len (1b+1b+1b+1b+max 12b max message) |  | gateway |  | 02190003;c8 TAG SetPoint=200 ->35192835;200;0;0
002F | 23 03 00 06 02 00 00 00; | send.modbus $type=tag $reg=6 $len=2 | 0x2b | Read modbus Acc[0]->Acc[*] | d d d: d; PUSH time Whi Whi: Dest+PosH+PosL+Len |  | gateway |  | Reat TAG Setpoint 35192835;0;0;0
0030 | 03 02 3D 00 00 00 00 00; | reuse #min_fan_speed_check | 0x30 | Call RCU Acc[*] | 0x82 Dest Type: Dest; PUSH time Whi Whi: Program address |  | Pass 4 register to the defined RCU device (+read ModBus 3 su TCP/IP)
0031 | 10 80 01 00 32 00 5E 01; | load $dec=65536*35*10+5*10
0032 | 10 81 0A 00 04 00 00 00; | save $var=anti_ice | # | Notify packet | d d d: Parameters
0033 | 10 80 01 00 01 00 05 00; | load $dec=65536*0.5*10+0.1*10 | 1 | Eartbeat | d d d: Counter
0034 | 10 81 0A 00 13 00 00 00; | save $var=intervention | 2 | Card Insert | d d d: CardId (8), Time
0035 | 21 03 00 03 00 02 00 00; | send.modbus $type=tag $reg=3 $dec=2 | 3 | CardExtract | d d d: none
0036 | 01 01 00 00 64 00 00 00; | wait $sec=0.01 | 4 | Mur/Dnd | d d d: Status
0037 | 21 03 00 08 00 02 00 00; | send.modbus $type=tag $reg=8 $hex=2 | 5 | OpenNOK | d d d: Status, Time
0038 | 10 80 0A 00 15 00 00 00; | load $var=user | 6 | Open OK | d d d: CardId (8), Time
0039 | 05 01 45 00 00 00 00 00; | if not equal #refresh_tag1 $hex=0 | 7 | Read RTC Var | bar: d d d to PUSH time PosLo PosLo
003A | 10 80 01 00 80 00 00 00; | load $hex=80 | 8 | Read modbus from device | bar: d d d to PUSH time PosLo PosLo
003B | 23 03 00 0D 04 00 00 00; | send.modbus $type=tag $reg=13 $len=4 | bar: d d d to PUSH time PosLo PosLo
003C | 04 01 00 00 00 00 00 00; | exit | bar: d d d to PUSH time PosLo PosLo
003D | 10 80 0A 00 15 00 00 00; | load $var=user | bar: d d d to PUSH time PosLo PosLo
003E | 09 01 42 00 FF 00 00 00; | if bit true #+4 $hex=ff
003F | 10 80 01 00 01 00 00 00; | load $hex=01
0040 | 10 81 0A 00 12 00 00 00; | save $var=season
0041 | 04 01 00 00 00 00 00 00; | exit
0042 | 10 80 01 00 11 00 00 00; | load $hex=11
0043 | 10 81 0A 00 12 00 00 00; | save $var=season
0044 | 04 01 00 00 00 00 00 00; | exit
0045 | 10 80 0A 00 06 00 00 00; | load $var=thermo1
0046 | 10 06 01 00 AA AA 00 00; | math.and $hex=aaaa
0047 | 08 01 49 00 80 00 00 00; | if equal #+2 $hex=80
0048 | 10 08 01 00 01 00 00 00; | math.shiftr $dec=1
0049 | 22 03 00 0D 04 00 00 00; | send.modbus $dev=tag1 $reg=13 $len=4
004A | 04 01 00 00 00 00 00 00; | exit
004B | 10 80 01 00 01 06 00 00; | load $hex=0601
004C | 10 81 12 00 03 00 00 00; | save modbus $var=m_fcu_speed
004D | 10 80 01 00 55 06 3F 00; | load $fan=fan1
004E | 01 01 62 00 00 00 00 00; | goto #tag1_common
004F | 10 80 01 00 02 06 00 00; | load $hex=0602
0050 | 10 81 12 00 03 00 00 00; | save modbus $var=m_fcu_speed
0051 | 10 80 01 00 65 05 3F 00; | load $fan=fan2
0052 | 01 01 62 00 00 00 00 00; | goto #tag1_common
0053 | 10 80 01 00 03 06 00 00; | load $hex=0603
0054 | 10 81 12 00 03 00 00 00; | save modbus $var=m_fcu_speed
0055 | 10 80 01 00 56 05 3F 00; | load $fan=fan3
0056 | 01 01 62 00 00 00 00 00; | goto #tag1_common
0057 | 10 80 01 00 04 06 00 00; | load $hex=0604
0058 | 10 81 12 00 03 00 00 00; | save modbus $var=m_fcu_speed
0059 | 10 80 01 00 55 09 3F 00; | load $fan=auto
005A | 01 01 62 00 00 00 00 00; | goto #tag1_common
005B | 10 80 01 00 05 06 00 00; | load $hex=0605
005C | 10 81 12 00 03 00 00 00; | save modbus $var=m_fcu_speed
005D | 10 80 01 00 95 05 3F 00; | load $fan=eco
005E | 01 01 62 00 00 00 00 00; | goto #tag1_common
005F | 10 80 01 00 06 06 00 00; | load $hex=0606
0060 | 10 81 12 00 03 00 00 00; | save modbus $var=m_fcu_speed
0061 | 10 80 01 00 59 05 3F 00; | load $fan=off
0062 | 10 81 0A 00 06 00 00 00; | save $var=thermo1
0063 | 22 03 00 0D 04 00 00 00; | send.modbus $dev=tag1 $reg=13 $len=4
0064 | 03 02 45 00 F0 49 02 00; | reuse #refresh_tag1 $sec=15
0065 | 04 01 00 00 00 00 00 00; | exit
0066 | 10 80 0A 00 06 00 00 00; | load $var=thermo1
0067 | 22 03 00 0D 04 00 00 00; | send.modbus $dev=tag1 $reg=13 $len=4
0068 | 03 02 45 00 F0 49 02 00; | reuse #refresh_tag1 $sec=15
0069 | 04 01 00 00 00 00 00 00; | exit
006A | 03 02 66 00 00 00 00 00; | reuse #tag1_wakeup
006B | 01 01 00 00 60 EA 00 00; | wait $sec=6
006C | 26 03 00 19 02 00 00 00; | read.modbus $dev=tag1 $reg=25
006D | 10 81 0A 00 0C 00 00 00; | save $var=temp1
006E | 10 81 12 00 04 00 00 00; | save modbus $var=m_fcu_setpoint
006F | 04 01 00 00 00 00 00 00; | exit
0070 | 01 01 00 00 20 4E 00 00; | wait $sec=2
0071 | 10 80 0A 00 14 00 00 00; | load $var=room_empty
0072 | 07 01 75 00 00 80 00 00; | if less than #+3 $hex=8000
0073 | 10 06 01 00 FF 7F FF FF; | math.and $relay=16
0074 | 10 01 0A 00 0C 00 00 00; | math.add $var=temp1
0075 | 22 03 00 19 02 00 00 00; | send.modbus $dev=tag1 $reg=25 $len=2
0076 | 04 01 00 00 00 00 00 00; | exit
0077 | 26 03 00 09 02 00 00 00; | read.modbus $dev=tag1 $reg=9
0078 | 10 81 12 00 05 00 00 00; | save modbus $var=m_current_temp
0079 | 01 01 77 00 80 8D 5B 00; | goto #tag1_current_temp $min=10
007A | 03 02 7C 00 10 27 00 00; | reuse #use_send_rcu_relays $sec=1
007B | 04 01 00 00 00 00 00 00; | exit
007C | 02 03 00 00 00 00 00 00; | rcu.read relays
007D | 10 81 12 00 02 00 00 00; | save modbus $var=m_rcu_relays
007E | 04 01 00 00 00 00 00 00; | exit
007F | 08 01 86 00 00 00 00 00; | if equal #modbus_user_receive $dec=0
0080 | 08 01 9B 00 01 00 00 00; | if equal #modbus_workflow_receive $dec=1
0081 | 08 01 9E 00 02 00 00 00; | if equal #modbus_receive_rcu_relays $dec=2
0082 | 08 01 A6 00 04 00 00 00; | if equal #modbus_receive_tag_fan $dec=4
0083 | 08 01 AB 00 05 00 00 00; | if equal #modbus_receive_tag_temp $dec=5
0084 | 08 01 AF 00 06 00 00 00; | if equal #modbus_receive_bell $dec=6
0085 | 04 01 00 00 00 00 00 00; | exit
0086 | 10 80 12 00 00 00 00 00; | load modbus $var=m_user
0087 | 10 81 0A 00 15 00 00 00; | save $var=user
0088 | 08 01 8F 00 00 00 00 00; | if equal #tag_without_user $hex=0
0089 | 10 80 0A 00 0C 00 00 00; | load $var=temp1
008A | 23 03 00 19 02 00 00 00; | send.modbus $type=tag $reg=25 $len=2
008B | 03 03 45 00 00 00 00 03; | reuse #refresh_tag1 $dev=tag1
008C | 10 80 01 00 11 00 00 00; | load $hex=11
008D | 10 81 0A 00 12 00 00 00; | save $var=season
008E | 04 01 00 00 00 00 00 00; | exit
008F | 03 03 45 00 00 00 00 03; | reuse #refresh_tag1 $dev=tag1
0090 | 10 80 0A 00 14 00 00 00; | load $var=room_empty
0091 | 07 01 94 00 00 80 00 00; | if less than #+3 $hex=8000
0092 | 10 06 01 00 FF 7F FF FF; | math.and $relay=16
0093 | 10 01 0A 00 0C 00 00 00; | math.add $var=temp1
0094 | 22 03 00 19 02 00 00 00; | send.modbus $dev=tag1 $reg=25 $len=2
0095 | 10 80 01 00 01 00 00 00; | load $hex=01
0096 | 10 81 0A 00 12 00 00 00; | save $var=season
0097 | 01 01 00 00 20 4E 00 00; | wait $sec=2
0098 | 10 80 01 00 80 00 00 00; | load $hex=80
0099 | 22 03 00 0D 04 00 00 00; | send.modbus $dev=tag1 $reg=13 $len=4
009A | 04 01 00 00 00 00 00 00; | exit
009B | 10 80 12 00 01 00 00 00; | load modbus $var=m_workflow
009C | 10 81 0A 00 16 00 00 00; | save $var=workflow
009D | 04 01 00 00 00 00 00 00; | exit
009E | 10 80 12 00 02 00 00 00; | load modbus $var=m_rcu_relays
009F | 10 06 01 00 78 FF FF FF; | math.and $relay=1-3,8
00A0 | 10 81 0A 00 81 00 00 00; | save $var=fcu_filter
00A1 | 02 03 00 00 00 00 00 00; | rcu.read relays
00A2 | 10 06 01 00 07 00 00 00; | math.and $relay=4-32
00A3 | 10 04 0A 00 81 00 00 00; | math.or $var=fcu_filter
00A4 | 02 04 00 00 00 00 00 00; | rcu.set all relays from acc
00A5 | 04 01 00 00 00 00 00 00; | exit
00A6 | 10 80 12 00 03 00 00 00; | load modbus $var=m_fcu_speed
00A7 | 10 04 01 00 00 00 3F 00; | math.or $hex=3f0000
00A8 | 10 81 0A 00 06 00 00 00; | save $var=thermo1
00A9 | 03 03 45 00 00 00 00 03; | reuse #refresh_tag1 $dev=tag1
00AA | 04 01 00 00 00 00 00 00; | exit
00AB | 10 80 12 00 04 00 00 00; | load modbus $var=m_fcu_setpoint
00AC | 10 81 0A 00 0C 00 00 00; | save $var=temp1
00AD | 22 03 00 19 02 00 00 00; | send.modbus $dev=tag1 $reg=25 $len=2
00AE | 04 01 00 00 00 00 00 00; | exit
00AF | 10 80 12 00 06 00 00 00; | load modbus $var=m_bell_ring
00B0 | 05 01 B4 00 01 00 00 00; | if not equal #exit $hex=1
00B1 | 02 09 01 00 80 00 00 00; | rcu.set $relay=8
00B2 | 01 01 00 00 08 07 00 00; | wait $sec=0.18
00B3 | 02 0A 01 00 80 00 00 00; | rcu.unset $relay=8
00B4 | 04 01 00 00 00 00 00 00; | exit
00B5 | 26 0B 00 03 02 00 00 00; | read.modbus $dev=11 $reg=3
00B6 | 08 0A B9 00 82 00 00 00; | if equal goto #+3 $var=pt100_7_water_return
00B7 | 10 81 0A 00 82 00 00 00; | save $var=pt100_7_water_return
00B8 | 10 81 12 00 07 00 00 00; | save modbus $var=m_pt100_7_water_return
00B9 | 01 01 00 00 E0 93 04 00; | wait $sec=30
00BA | 26 0B 00 04 02 00 00 00; | read.modbus $dev=11 $reg=4
00BB | 08 0A BE 00 83 00 00 00; | if equal goto #+3 $var=pt100_7_water_supply
00BC | 10 81 0A 00 83 00 00 00; | save $var=pt100_7_water_supply
00BD | 10 81 12 00 08 00 00 00; | save modbus $var=m_pt100_7_water_supply
00BE | 01 01 00 00 E0 93 04 00; | wait $sec=30
00BF | 26 0B 00 05 02 00 00 00; | read.modbus $dev=11 $reg=5
00C0 | 08 0A C3 00 84 00 00 00; | if equal goto #+3 $var=pt100_7_air_return
00C1 | 10 81 0A 00 84 00 00 00; | save $var=pt100_7_air_return
00C2 | 10 81 12 00 09 00 00 00; | save modbus $var=m_pt100_7_air_return
00C3 | 01 01 00 00 E0 93 04 00; | wait $sec=30
00C4 | 26 0B 00 06 02 00 00 00; | read.modbus $dev=11 $reg=6
00C5 | 08 0A C8 00 85 00 00 00; | if equal goto #+3 $var=pt100_7_air_supply
00C6 | 10 81 0A 00 85 00 00 00; | save $var=pt100_7_air_supply
00C7 | 10 81 12 00 0A 00 00 00; | save modbus $var=m_pt100_7_air_supply
00C8 | 01 01 B5 00 40 77 1B 00; | goto #temp_probe_cycle $min=3

## Settings4
00 | 02; | 2 | MAC Address | 1 |  |  |  |  | Dir: | C:\tini\ModularHotel\ABSlink\RCUmanager\bin\Release
01 | 01; | 1 |  | 2 |  |  |  |  | Settings page: | 0x0007D000
02 | 36; | 54 |  | 3 |  | 19
03 | 7D; | 125 |  | 4 |  | 109
04 | 6D; | 109 |  | 5 |  | 125
05 | 14; | 19 |  | 6 |  | 54
06 | C0; | 192 | Device IP | 1
07 | A8; | 168 |  | 2
08 | 01; | 1 |  | 3
09 | E0; | 224 |  | 4
0A | FF; | 255 | Mask | 1
0B | FF; | 255 |  | 2
0C | FF; | 255 |  | 3
0D | 00; | 0 |  | 4
0E | 82; | 130 | Gateway | 1
0F | 0A; | 10 |  | 2
10 | 01; | 1 |  | 3
11 | 01; | 1 |  | 4
12 | 10; | 16 | Port | Hi | 4096
13 | 00; | 0 |  | Low
14 | 00; | 0 | Devices/EventMap | 1 |  | Device list followed by event map
15 | C0; | 192 |  | 2 |  | (align 4 byte var/dest)
16 | 07; | 7 |  | 3
17 | 00; | 0 |  | 4
18 | 00; | 0 | AutoStart/Program | 1 |  | Autostart followed by program
19 | 80; | 128 | 0=above 63 blocks 80=standard below 63 blocks | 2 |  | (align 4 byte var/dest)
1A | 07; | 7 |  | 3
1B | 00; | 0 |  | 4
1C | 14; | 20 | DeviceNum | 4 |  | Devices number
1D | 04; | 4 | AutostartNum | Space |  | Number of elements in autoexec
1E | 82; | 130 | TH Server | 1 |  | ModBus pseudoadd FF
1F | 0A; | 10 |  | 2
20 | 01; | 1 |  | 3
21 | DC; | 220 |  | 4
22 | E8; | 232 | Site code | 1
23 | 03; | 3 |  | 2
24 | 00; | 0 |  | 3
25 | 00; | 0 |  | 4
26 | 00; | 0 |  | 5
27 | 00; | 0 |  | 6
28 | 00; | 0 |  | 7
29 | 00; | 0 |  | 8
2A | 81; | 129 | Room number | 1
2B | 00; | 0 |  | 2
2C | 00; | 0 | Building/Extension | 1
2D | 00; | 0 |  | 2
2E | 10; | 16 | TH server port | 1
2F | 00; | 0 |  | 2
30 | 53; | 83 | COM1 | Type |  | Master 115k | Processes sheet
31 | 53; | 83 | COM2 | Type |  | Master 115k
32 | D0; | 83 | COM3 | Type |  | Master 9.6k
33 | 00; | 0 | RF | Type |  | Slave 9600
34 | 01; | 1 | TCP/IP | Type |  | Slave
35 | 14; | 20 | COMTimeout | Par secs |  | Max timeout on answer (in 128 1/10000 secs, 20 =1/4 secs)
36 | 5A; | 90 | COM Delay 1 | Tick |  | Delay between packets
37 | 32; | 50 | COM Delay 1 | Tick |  | Delay between packets
38 | 20; | 32 | COM Delay 1 | Tick |  | Delay between packets
39 | 07; | 7 | RCU Relay mask |  |  | security block, filter out thermo relays
3A | 03; | 3 | Thermo1 | Device Num |  | TAG
3B | 01; | 1 | Thermo1 | Type |  | 0=Null, 1=TAG base rel 1/0
3C | 00; | 0 | Thermo1 | Control device |  | 0=RCU, #=device num |  |  |  | 3 | open
3D | 00; | 0 | Thermo1 | Hot relay |  | 0=Null, 1-31 = rel, 32-33 = 0-10V |  |  |  | 4 | close
3E | 20; | 32 | Thermo1 | Cold relay |  | 0=Null, 1-31 = rel, 32-33 = 0-10V
3F | 01; | 1 | Thermo1 | Speed1 relay |  | 0=Null, 1-31 = rel
40 | 02; | 2 | Thermo1 | Speed2 relay |  | 0=Null, 1-31 = rel |  |  |  | 10010011 | 93;
41 | 03; | 3 | Thermo1 | Speed3 relay |  | 0=Null, 1-31 = rel
42 | 00; | 0 | Thermo1 | Window contact |  | 87th bits 00Rcu/01Tag/10Dev, 20h=0NO 1NC, 00hNone, 0fh #Input
43 | 00; | 0 | Thermo2 | Device Num |  | TAG
44 | 00; | 0 | Thermo2 | Type |  | 0=Null, 1=TAG base rel 1/0
45 | 00; | 0 | Thermo2 | Control device |  | 0=RCU, #=device num
46 | 00; | 0 | Thermo2 | Hot relay |  | 0=Null, 1-31 = rel, 32-33 = 0-10V
47 | 00; | 0 | Thermo2 | Cold relay |  | 0=Null, 1-31 = rel, 32-33 = 0-10V
48 | 00; | 0 | Thermo2 | Speed1 relay |  | 0=Null, 1-31 = rel
49 | 00; | 0 | Thermo2 | Speed2 relay |  | 0=Null, 1-31 = rel
4A | 00; | 0 | Thermo2 | Speed3 relay |  | 0=Null, 1-31 = rel
4B | 00; | 0 | Thermo2 | Window contact |  | 87th bits 00Rcu/01Tag/10Dev, 00hNone, #Input number
4C | 00; | 0 | Thermo3 | Device Num |  | TAG
4D | 00; | 0 | Thermo3 | Type |  | 0=Null, 1=TAG base rel 1/0
4E | 00; | 0 | Thermo3 | Control device |  | 0=RCU, #=device num
4F | 00; | 0 | Thermo3 | Hot relay |  | 0=Null, 1-31 = rel, 32-33 = 0-10V
50 | 00; | 0 | Thermo3 | Cold relay |  | 0=Null, 1-31 = rel, 32-33 = 0-10V
51 | 00; | 0 | Thermo3 | Speed1 relay |  | 0=Null, 1-31 = rel
52 | 00; | 0 | Thermo3 | Speed2 relay |  | 0=Null, 1-31 = rel
53 | 00; | 0 | Thermo3 | Speed3 relay |  | 0=Null, 1-31 = rel
54 | 00; | 0 | Thermo3 | Window contact |  | 87th bits 00Rcu/01Tag/10Dev, 00hNone, #Input number
55 | 00; | 0 | Thermo4 | Device Num |  | TAG
56 | 00; | 0 | Thermo4 | Type |  | 0=Null, 1=TAG base rel 1/0
57 | 00; | 0 | Thermo4 | Control device |  | 0=RCU, #=device num
58 | 00; | 0 | Thermo4 | Hot relay |  | 0=Null, 1-31 = rel, 32-33 = 0-10V
59 | 00; | 0 | Thermo4 | Cold relay |  | 0=Null, 1-31 = rel, 32-33 = 0-10V
5A | 00; | 0 | Thermo4 | Speed1 relay |  | 0=Null, 1-31 = rel
5B | 00; | 0 | Thermo4 | Speed2 relay |  | 0=Null, 1-31 = rel
5C | 00; | 0 | Thermo4 | Speed3 relay |  | 0=Null, 1-31 = rel
5D | 00; | 0 | Thermo4 | Window contact |  | 87th bits 00Rcu/01Tag/10Dev, 00hNone, #Input number
5E | 00; | 0 | Thermo5 | Device Num |  | TAG
5F | 00; | 0 | Thermo5 | Type |  | 0=Null, 1=TAG base rel 1/0
60 | 00; | 0 | Thermo5 | Control device |  | 0=RCU, #=device num
61 | 00; | 0 | Thermo5 | Hot relay |  | 0=Null, 1-31 = rel, 32-33 = 0-10V
62 | 00; | 0 | Thermo5 | Cold relay |  | 0=Null, 1-31 = rel, 32-33 = 0-10V
63 | 00; | 0 | Thermo5 | Speed1 relay |  | 0=Null, 1-31 = rel
64 | 00; | 0 | Thermo5 | Speed2 relay |  | 0=Null, 1-31 = rel
65 | 00; | 0 | Thermo5 | Speed3 relay |  | 0=Null, 1-31 = rel
66 | 00; | 0 | Thermo5 | Window contact |  | 87th bits 00Rcu/01Tag/10Dev, 00hNone, #Input number
67 | 00; | 0 | Thermo6 | Device Num |  | TAG
68 | 00; | 0 | Thermo6 | Type |  | 0=Null, 1=TAG base rel 1/0
69 | 00; | 0 | Thermo6 | Control device |  | 0=RCU, #=device num
6A | 00; | 0 | Thermo6 | Hot relay |  | 0=Null, 1-31 = rel, 32-33 = 0-10V
6B | 00; | 0 | Thermo6 | Cold relay |  | 0=Null, 1-31 = rel, 32-33 = 0-10V
6C | 00; | 0 | Thermo6 | Speed1 relay |  | 0=Null, 1-31 = rel
6D | 00; | 0 | Thermo6 | Speed2 relay |  | 0=Null, 1-31 = rel
6E | 00; | 0 | Thermo6 | Speed3 relay |  | 0=Null, 1-31 = rel
6F | 00; | 0 | Thermo6 | Window contact |  | 8th bit 0Rcu/1Tag, 0None, #Input number
70 | 14; | 20 | Thermo* | Speed Ratio |  | FanSpeed=Temperature delta in decimals / ratio
71 | 01; | 1 | Thermo* | Valve Ratio |  | Valve 0-100%= delta temp in cent / ratio
72 | 00; | 0
73 | 00; | 0
74 | 00; | 0 | Thermo* | RunTime Cold | 1 | Running time for the valve in TICK
75 | 00; | 0 | Thermo* | RunTime Cold | 2 | es. 190 sec= 10000*190
76 | 00; | 0 | Thermo* | RunTime Cold | 3 |  | 0 | 00000000
77 | 00; | 0 | Thermo* | RunTime Cold | 4
78 | 00; | 0 | Thermo* | RunTime Hot | 1
79 | 00; | 0 | Thermo* | RunTime Hot | 2
7A | 00; | 0 | Thermo* | RunTime Hot | 3 |  | 0 | 00000000
7B | 00; | 0 | Thermo* | RunTime Hot | 4
7C | 00; | 0
7D | 00; | 0
7E | 00; | 0
7F | 01; | 1
80 | 10; | 16 | Roles opening door | low |  | Permit to define staff open the door
81 | 00; | 0 | Roles opening door | high
82 | 01; | 1 | Ablitate groups opening |  |  | bit1=true
83 | 18; | 24 | Roles blocked by | low |  | HK and HKS
84 | 00; | 0 | flag on event | high
85 | 00; | 0 | RfId mode |  |  | 0=standard, 1=Vingcard mixed
86 | 00; | 0 | RfId data |  |  | On Vingcard mode = starting info for staff
87 | 00; | 0
88 | 01; | 1 | Type of calculation for open valve |  |  | 0=standard, 1=japanese algorithm
89 | 00; | 0
8A | 01; | 1 | Battery if=1 from program, if=0 charging |  |  | bit 0=0 Output on, 1=0 if battery dor lock 100% to-do add new HW
8B | 00; | 0 | Delay on server error |  |  | amount of delay before next send, 0=1 second else (1/10000)<<val
8C | 00; | 0 | FAN remap on valve mode |  |  | 1= fan based on valves according the remap table below
8D | 00; | 0 | Fan1 Fan1 from valve %
8E | 00; | 0 | Fan2 Fan2 from valve %
8F | 00; | 0 | Fan3 Fan3 from valve %
90 | 03; | 3 | BSP1
91 | 00; | 0
92 | 01; | 1
93 | 80; | 128
94 | 00; | 0 | BSP2
95 | 00; | 0
96 | 00; | 0
97 | 00; | 0
98 | 00; | 0 | BSP3
99 | 00; | 0
9A | 00; | 0
9B | 00; | 0
9C | 00; | 0 | BSP4
9D | 00; | 0
9E | 00; | 0
9F | 00; | 0
A0 | 00; | 0 | BSP5
A1 | 00; | 0
A2 | 00; | 0
A3 | 00; | 0
A4 | 00; | 0 | BSP6
A5 | 00; | 0
A6 | 00; | 0
A7 | 00; | 0
A8 | 00; | 0
A9 | 00; | 0
AA | 00; | 0
AB | 00; | 0
AC | 00; | 0
AD | 00; | 0
AE | 00; | 0
AF | 00; | 0
B0 | 00; | 0
B1 | 00; | 0
B2 | 00; | 0
B3 | 00; | 0
B4 | 00; | 0
B5 | 00; | 0
B6 | 00; | 0
B7 | 00; | 0
B8 | 00; | 0
B9 | 00; | 0
BA | 00; | 0
BB | 00; | 0
BC | 00; | 0
BD | 00; | 0
BE | 00; | 0
BF | 00; | 0
C0 | 00; |  | COM4 BusExt |  | !=0 = Activate |  | 3D-5D Kaba - 50 WiFi -10.50.53 ZigBee master 50 vingcard;
C1 | 00; | 1 | COM Ext Type |  | 0, 1=Kaba, 2=WiFi/ZigBee transparent, 3=ZigBeeMaster, 4=WiFiMaster Digi API
C2 | 01; | 1 | Expansio bus type |  | 1=COM, 2=8 relays
C3 | 00; | 0 | Number of locks |  | Address specified on ZigBee addresses from 0x300
C4 | 00; | 0 | ZeroCrossing on Input 8 | 1 | Delay RelayOn/Off on zero crossing (1 activate, >1 delay in TICK)
C5 | 00; | 0 | ZeroCrossing on Input | 2
C6 | 00; | 0 | ZeroCrossing on Input | 3
C7 | 00; | 0 | ZeroCrossing on Input | 4
C8 | 00; | 0 | Offset GMT time -> UTC | 1 | Offset signed INT 32 bit
C9 | 00; | 0 | params set to AUS time | 2 |  | 0 | GMT
CA | 00; | 0 |  | 3 |  | 0 | val
CB | 00; | 0 |  | 4 |  |  | FFFFFFFF-hex(GMT *3600)
CC | 00; | 0
CD | 00; | 0
CE | 00; | 0
CF | 00; | 0
D0 | 00; | 0
D1 | 00; | 0
D2 | 00; | 0
D3 | 00; | 0
D4 | 00; | 0
D5 | 00; | 0
D6 | 00; | 0
D7 | 00; | 0
D8 | 00; | 0
D9 | 00; | 0
DA | 00; | 0
DB | 00; | 0
DC | 00; | 0
DD | 00; | 0
DE | 00; | 0
DF | 00; | 0
E0 | 00; | 0
E1 | 00; | 0
E2 | 00; | 0
E3 | 00; | 0
E4 | 00; | 0
E5 | 00; | 0
E6 | 00; | 0
E7 | 00; | 0
E8 | 00; | 0
E9 | 00; | 0
EA | 00; | 0
EB | 00; | 0
EC | 00; | 0
ED | 00; | 0
EE | 00; | 0
EF | 00; | 0
F0 | 00; | 0
F1 | 00; | 0
F2 | 00; | 0
F3 | 00; | 0
F4 | 00; | 0
F5 | 00; | 0
F6 | 00; | 0
F7 | 00; | 0
F8 | 00; | 0
F9 | 00; | 0
FA | 00; | 0
FB | 00; | 0
FC | 00; | 0
FD | 00; | 0
FE | 00; | 0
FF | 00; | 0
100 | 02; | 2 | Enabled groups |  | 0 |  | Group | 000-007
101 | 00; | 0 |  |  | 1 |  |  | 008-015
102 | 00; | 0 |  |  | 2 |  |  | 016-023
103 | 00; | 0 |  |  | 3
104 | 00; | 0 |  |  | 4
105 | 00; | 0 |  |  | 5
106 | 00; | 0 |  |  | 6
107 | 00; | 0 |  |  | 7
108 | 00; | 0 |  |  | 8
109 | 00; | 0 |  |  | 9
10A | 00; | 0 |  |  | 10
10B | 00; | 0 |  |  | 11
10C | 00; | 0 |  |  | 12
10D | 00; | 0 |  |  | 13
10E | 00; | 0 |  |  | 14
10F | 00; | 0 |  |  | 15
110 | 00; | 0 |  |  | 16
111 | 00; | 0 |  |  | 17
112 | 00; | 0 |  |  | 18
113 | 00; | 0 |  |  | 19
114 | 00; | 0 |  |  | 20
115 | 00; | 0 |  |  | 21
116 | 00; | 0 |  |  | 22
117 | 00; | 0 |  |  | 23
118 | 00; | 0 |  |  | 24
119 | 00; | 0 |  |  | 25
11A | 00; | 0 |  |  | 26
11B | 00; | 0 |  |  | 27
11C | 00; | 0 |  |  | 28
11D | 00; | 0 |  |  | 29
11E | 00; | 0 |  |  | 30
11F | 00; | 0 |  |  | 31 |  |  | 248-255
120 | 00; | 0
121 | 00; | 0
122 | 00; | 0
123 | 00; | 0
124 | 00; | 0
125 | 00; | 0
126 | 00; | 0
127 | 00; | 0
128 | 00; | 0
129 | 00; | 0
12A | 00; | 0
12B | 00; | 0
12C | 00; | 0
12D | 00; | 0
12E | 00; | 0
12F | 00; | 0
130 | 00; | 0
131 | 00; | 0
132 | 00; | 0
133 | 00; | 0
134 | 00; | 0
135 | 00; | 0
136 | 00; | 0
137 | 00; | 0
138 | 00; | 0
139 | 00; | 0
13A | 00; | 0
13B | 00; | 0
13C | 00; | 0
13D | 00; | 0
13E | 00; | 0 |  |  | 30
13F | 00; | 0 |  |  | 31 |  |  | 248-255
140 | 02; | 2 | Enabled groups IDPG2 |  | 0 |  | Group | 000-007
141 | 00; | 0 |  |  | 1 |  |  | 008-015
142 | 00; | 0 |  |  | 2 |  |  | 016-023
143 | 00; | 0 |  |  | 3
144 | 00; | 0 |  |  | 4
145 | 00; | 0 |  |  | 5
146 | 00; | 0 |  |  | 6
147 | 00; | 0 |  |  | 7
148 | 00; | 0 |  |  | 8
149 | 00; | 0 |  |  | 9
14A | 00; | 0 |  |  | 10
14B | 00; | 0 |  |  | 11
14C | 00; | 0 |  |  | 12
14D | 00; | 0 |  |  | 13
14E | 00; | 0 |  |  | 14
14F | 00; | 0 |  |  | 15
150 | 00; | 0 |  |  | 16
151 | 00; | 0 |  |  | 17
152 | 00; | 0 |  |  | 18
153 | 00; | 0 |  |  | 19
154 | 00; | 0 |  |  | 20
155 | 00; | 0 |  |  | 21
156 | 00; | 0 |  |  | 22
157 | 00; | 0 |  |  | 23
158 | 00; | 0 |  |  | 24
159 | 00; | 0 |  |  | 25
15A | 00; | 0 |  |  | 26
15B | 00; | 0 |  |  | 27
15C | 00; | 0 |  |  | 28
15D | 00; | 0 |  |  | 29
15E | 00; | 0 |  |  | 30
15F | 00; | 0 |  |  | 31 |  |  | 248-255
160 | 02; | 2 | Enabled groups IDPG3 |  | 0 |  | Group | 000-007
161 | 00; | 0 |  |  | 1 |  |  | 008-015
162 | 00; | 0 |  |  | 2 |  |  | 016-023
163 | 00; | 0 |  |  | 3
164 | 00; | 0 |  |  | 4
165 | 00; | 0 |  |  | 5
166 | 00; | 0 |  |  | 6
167 | 00; | 0 |  |  | 7
168 | 00; | 0 |  |  | 8
169 | 00; | 0 |  |  | 9
16A | 00; | 0 |  |  | 10
16B | 00; | 0 |  |  | 11
16C | 00; | 0 |  |  | 12
16D | 00; | 0 |  |  | 13
16E | 00; | 0 |  |  | 14
16F | 00; | 0 |  |  | 15
170 | 00; | 0 |  |  | 16
171 | 00; | 0 |  |  | 17
172 | 00; | 0 |  |  | 18
173 | 00; | 0 |  |  | 19
174 | 00; | 0 |  |  | 20
175 | 00; | 0 |  |  | 21
176 | 00; | 0 |  |  | 22
177 | 00; | 0 |  |  | 23
178 | 00; | 0 |  |  | 24
179 | 00; | 0 |  |  | 25
17A | 00; | 0 |  |  | 26
17B | 00; | 0 |  |  | 27
17C | 00; | 0 |  |  | 28
17D | 00; | 0 |  |  | 29
17E | 00; | 0 |  |  | 30
17F | 00; | 0 |  |  | 31 |  |  | 248-255
180 | 02; | 2 | Enabled groups IDPG4 |  | 0 |  | Group | 000-007
181 | 00; | 0 |  |  | 1 |  |  | 008-015
182 | 00; | 0 |  |  | 2 |  |  | 016-023
183 | 00; | 0 |  |  | 3
184 | 00; | 0 |  |  | 4
185 | 00; | 0 |  |  | 5
186 | 00; | 0 |  |  | 6
187 | 00; | 0 |  |  | 7
188 | 00; | 0 |  |  | 8
189 | 00; | 0 |  |  | 9
18A | 00; | 0 |  |  | 10
18B | 00; | 0 |  |  | 11
18C | 00; | 0 |  |  | 12
18D | 00; | 0 |  |  | 13
18E | 00; | 0 |  |  | 14
18F | 00; | 0 |  |  | 15
190 | 00; | 0 |  |  | 16
191 | 00; | 0 |  |  | 17
192 | 00; | 0 |  |  | 18
193 | 00; | 0 |  |  | 19
194 | 00; | 0 |  |  | 20
195 | 00; | 0 |  |  | 21
196 | 00; | 0 |  |  | 22
197 | 00; | 0 |  |  | 23
198 | 00; | 0 |  |  | 24
199 | 00; | 0 |  |  | 25
19A | 00; | 0 |  |  | 26
19B | 00; | 0 |  |  | 27
19C | 00; | 0 |  |  | 28
19D | 00; | 0 |  |  | 29
19E | 00; | 0 |  |  | 30
19F | 00; | 0 |  |  | 31 |  |  | 248-255
1A0 | 02; | 2 | Enabled groups IDPG5 |  | 0 |  | Group | 000-007
1A1 | 00; | 0 |  |  | 1 |  |  | 008-015
1A2 | 00; | 0 |  |  | 2 |  |  | 016-023
1A3 | 00; | 0 |  |  | 3
1A4 | 00; | 0 |  |  | 4
1A5 | 00; | 0 |  |  | 5
1A6 | 00; | 0 |  |  | 6
1A7 | 00; | 0 |  |  | 7
1A8 | 00; | 0 |  |  | 8
1A9 | 00; | 0 |  |  | 9
1AA | 00; | 0 |  |  | 10
1AB | 00; | 0 |  |  | 11
1AC | 00; | 0 |  |  | 12
1AD | 00; | 0 |  |  | 13
1AE | 00; | 0 |  |  | 14
1AF | 00; | 0 |  |  | 15
1B0 | 00; | 0 |  |  | 16
1B1 | 00; | 0 |  |  | 17
1B2 | 00; | 0 |  |  | 18
1B3 | 00; | 0 |  |  | 19
1B4 | 00; | 0 |  |  | 20
1B5 | 00; | 0 |  |  | 21
1B6 | 00; | 0 |  |  | 22
1B7 | 00; | 0 |  |  | 23
1B8 | 00; | 0 |  |  | 24
1B9 | 00; | 0 |  |  | 25
1BA | 00; | 0 |  |  | 26
1BB | 00; | 0 |  |  | 27
1BC | 00; | 0 |  |  | 28
1BD | 00; | 0 |  |  | 29
1BE | 00; | 0 |  |  | 30
1BF | 00; | 0 |  |  | 31 |  |  | 248-255
1C0 | 02; | 2 | Enabled groups IDPG6 |  | 0 |  | Group | 000-007
1C1 | 00; | 0 |  |  | 1 |  |  | 008-015
1C2 | 00; | 0 |  |  | 2 |  |  | 016-023
1C3 | 00; | 0 |  |  | 3
1C4 | 00; | 0 |  |  | 4
1C5 | 00; | 0 |  |  | 5
1C6 | 00; | 0 |  |  | 6
1C7 | 00; | 0 |  |  | 7
1C8 | 00; | 0 |  |  | 8
1C9 | 00; | 0 |  |  | 9
1CA | 00; | 0 |  |  | 10
1CB | 00; | 0 |  |  | 11
1CC | 00; | 0 |  |  | 12
1CD | 00; | 0 |  |  | 13
1CE | 00; | 0 |  |  | 14
1CF | 00; | 0 |  |  | 15
1D0 | 00; | 0 |  |  | 16
1D1 | 00; | 0 |  |  | 17
1D2 | 00; | 0 |  |  | 18
1D3 | 00; | 0 |  |  | 19
1D4 | 00; | 0 |  |  | 20
1D5 | 00; | 0 |  |  | 21
1D6 | 00; | 0 |  |  | 22
1D7 | 00; | 0 |  |  | 23
1D8 | 00; | 0 |  |  | 24
1D9 | 00; | 0 |  |  | 25
1DA | 00; | 0 |  |  | 26
1DB | 00; | 0 |  |  | 27
1DC | 00; | 0 |  |  | 28
1DD | 00; | 0 |  |  | 29
1DE | 00; | 0 |  |  | 30
1DF | 00; | 0 |  |  | 31 |  |  | 248-255
1E0 | 02; | 2 | Enabled groups IDPG7 |  | 0 |  | Group | 000-007
1E1 | 00; | 0 |  |  | 1 |  |  | 008-015
1E2 | 00; | 0 |  |  | 2 |  |  | 016-023
1E3 | 00; | 0 |  |  | 3
1E4 | 00; | 0 |  |  | 4
1E5 | 00; | 0 |  |  | 5
1E6 | 00; | 0 |  |  | 6
1E7 | 00; | 0 |  |  | 7
1E8 | 00; | 0 |  |  | 8
1E9 | 00; | 0 |  |  | 9
1EA | 00; | 0 |  |  | 10
1EB | 00; | 0 |  |  | 11
1EC | 00; | 0 |  |  | 12
1ED | 00; | 0 |  |  | 13
1EE | 00; | 0 |  |  | 14
1EF | 00; | 0 |  |  | 15
1F0 | 00; | 0 |  |  | 16
1F1 | 00; | 0 |  |  | 17
1F2 | 00; | 0 |  |  | 18
1F3 | 00; | 0 |  |  | 19
1F4 | 00; | 0 |  |  | 20
1F5 | 00; | 0 |  |  | 21
1F6 | 00; | 0 |  |  | 22
1F7 | 00; | 0 |  |  | 23
1F8 | 00; | 0 |  |  | 24
1F9 | 00; | 0 |  |  | 25
1FA | 00; | 0 |  |  | 26
1FB | 00; | 0 |  |  | 27
1FC | 00; | 0 |  |  | 28
1FD | 00; | 0 |  |  | 29
1FE | 00; | 0 |  |  | 30
1FF | 00; | 0 |  |  | 31 |  |  | 248-255
200 | 00; | 0
201 | 00; | 0
202 | 00; | 0
203 | 00; | 0
204 | 00; | 0
205 | 00; | 0
206 | 00; | 0
207 | 00; | 0
208 | 00; | 0
209 | 00; | 0
20A | 00; | 0
20B | 00; | 0
20C | 00; | 0
20D | 00; | 0
20E | 00; | 0
20F | 00; | 0
210 | 00; | 0
211 | 00; | 0
212 | 00; | 0
213 | 00; | 0
214 | 00; | 0
215 | 00; | 0
216 | 00; | 0
217 | 00; | 0
218 | 00; | 0
219 | 00; | 0
21A | 00; | 0
21B | 00; | 0
21C | 00; | 0
21D | 00; | 0
21E | 00; | 0
21F | 00; | 0
220 | 00; | 0
221 | 00; | 0
222 | 00; | 0
223 | 00; | 0
224 | 00; | 0
225 | 00; | 0
226 | 00; | 0
227 | 00; | 0
228 | 00; | 0
229 | 00; | 0
22A | 00; | 0
22B | 00; | 0
22C | 00; | 0
22D | 00; | 0
22E | 00; | 0
22F | 00; | 0
230 | 00; | 0
231 | 00; | 0
232 | 00; | 0
233 | 00; | 0
234 | 00; | 0
235 | 00; | 0
236 | 00; | 0
237 | 00; | 0
238 | 00; | 0
239 | 00; | 0
23A | 00; | 0
23B | 00; | 0
23C | 00; | 0
23D | 00; | 0
23E | 00; | 0
23F | 00; | 0
240 | 00; | 0
241 | 00; | 0
242 | 00; | 0
243 | 00; | 0
244 | 00; | 0
245 | 00; | 0
246 | 00; | 0
247 | 00; | 0
248 | 00; | 0
249 | 00; | 0
24A | 00; | 0
24B | 00; | 0
24C | 00; | 0
24D | 00; | 0
24E | 00; | 0
24F | 00; | 0
250 | 00; | 0
251 | 00; | 0
252 | 00; | 0
253 | 00; | 0
254 | 00; | 0
255 | 00; | 0
256 | 00; | 0
257 | 00; | 0
258 | 00; | 0
259 | 00; | 0
25A | 00; | 0
25B | 00; | 0
25C | 00; | 0
25D | 00; | 0
25E | 00; | 0
25F | 00; | 0
260 | 00; | 0
261 | 00; | 0
262 | 00; | 0
263 | 00; | 0
264 | 00; | 0
265 | 00; | 0
266 | 00; | 0
267 | 00; | 0
268 | 00; | 0
269 | 00; | 0
26A | 00; | 0
26B | 00; | 0
26C | 00; | 0
26D | 00; | 0
26E | 00; | 0
26F | 00; | 0
270 | 00; | 0
271 | 00; | 0
272 | 00; | 0
273 | 00; | 0
274 | 00; | 0
275 | 00; | 0
276 | 00; | 0
277 | 00; | 0
278 | 00; | 0
279 | 00; | 0
27A | 00; | 0
27B | 00; | 0
27C | 00; | 0
27D | 00; | 0
27E | 00; | 0
27F | 00; | 0
280 | 00; | 0
281 | 00; | 0
282 | 00; | 0
283 | 00; | 0
284 | 00; | 0
285 | 00; | 0
286 | 00; | 0
287 | 00; | 0
288 | 00; | 0
289 | 00; | 0
28A | 00; | 0
28B | 00; | 0
28C | 00; | 0
28D | 00; | 0
28E | 00; | 0
28F | 00; | 0
290 | 00; | 0
291 | 00; | 0
292 | 00; | 0
293 | 00; | 0
294 | 00; | 0
295 | 00; | 0
296 | 00; | 0
297 | 00; | 0
298 | 00; | 0
299 | 00; | 0
29A | 00; | 0
29B | 00; | 0
29C | 00; | 0
29D | 00; | 0
29E | 00; | 0
29F | 00; | 0
2A0 | 00; | 0
2A1 | 00; | 0
2A2 | 00; | 0
2A3 | 00; | 0
2A4 | 00; | 0
2A5 | 00; | 0
2A6 | 00; | 0
2A7 | 00; | 0
2A8 | 00; | 0
2A9 | 00; | 0
2AA | 00; | 0
2AB | 00; | 0
2AC | 00; | 0
2AD | 00; | 0
2AE | 00; | 0
2AF | 00; | 0
2B0 | 00; | 0
2B1 | 00; | 0
2B2 | 00; | 0
2B3 | 00; | 0
2B4 | 00; | 0
2B5 | 00; | 0
2B6 | 00; | 0
2B7 | 00; | 0
2B8 | 00; | 0
2B9 | 00; | 0
2BA | 00; | 0
2BB | 00; | 0
2BC | 00; | 0
2BD | 00; | 0
2BE | 00; | 0
2BF | 00; | 0
2C0 | 00; | 0
2C1 | 00; | 0
2C2 | 00; | 0
2C3 | 00; | 0
2C4 | 00; | 0
2C5 | 00; | 0
2C6 | 00; | 0
2C7 | 00; | 0
2C8 | 00; | 0
2C9 | 00; | 0
2CA | 00; | 0
2CB | 00; | 0
2CC | 00; | 0
2CD | 00; | 0
2CE | 00; | 0
2CF | 00; | 0
2D0 | 00; | 0
2D1 | 00; | 0
2D2 | 00; | 0
2D3 | 00; | 0
2D4 | 00; | 0
2D5 | 00; | 0
2D6 | 00; | 0
2D7 | 00; | 0
2D8 | 00; | 0
2D9 | 00; | 0
2DA | 00; | 0
2DB | 00; | 0
2DC | 00; | 0
2DD | 00; | 0
2DE | 00; | 0
2DF | 00; | 0
2E0 | 00; | 0
2E1 | 00; | 0
2E2 | 00; | 0
2E3 | 00; | 0
2E4 | 00; | 0
2E5 | 00; | 0
2E6 | 00; | 0
2E7 | 00; | 0
2E8 | 00; | 0
2E9 | 00; | 0
2EA | 00; | 0
2EB | 00; | 0
2EC | 00; | 0
2ED | 00; | 0
2EE | 00; | 0
2EF | 00; | 0
2F0 | 00; | 0
2F1 | 00; | 0
2F2 | 00; | 0
2F3 | 00; | 0
2F4 | 00; | 0
2F5 | 00; | 0
2F6 | 00; | 0
2F7 | 00; | 0
2F8 | 00; | 0
2F9 | 00; | 0
2FA | 00; | 0
2FB | 00; | 0
2FC | 00; | 0
2FD | 00; | 0
2FE | 00; | 0
2FF | 00; | 0
300 | 00; | 0
301 | 00; | 0
302 | 00; | 0
303 | 00; | 0
304 | 00; | 0
305 | 00; | 0
306 | 00; | 0
307 | 00; | 0
308 | 00; | 0
309 | 00; | 0
30A | 00; | 0
30B | 00; | 0
30C | 00; | 0
30D | 00; | 0
30E | 00; | 0
30F | 00; | 0
310 | 00; | 0
311 | 00; | 0
312 | 00; | 0
313 | 00; | 0
314 | 00; | 0
315 | 00; | 0
316 | 00; | 0
317 | 00; | 0
318 | 00; | 0
319 | 00; | 0
31A | 00; | 0
31B | 00; | 0
31C | 00; | 0
31D | 00; | 0
31E | 00; | 0
31F | 00; | 0
320 | 00; | 0
321 | 00; | 0
322 | 00; | 0
323 | 00; | 0
324 | 00; | 0
325 | 00; | 0
326 | 00; | 0
327 | 00; | 0
328 | 00; | 0
329 | 00; | 0
32A | 00; | 0
32B | 00; | 0
32C | 00; | 0
32D | 00; | 0
32E | 00; | 0
32F | 00; | 0
330 | 00; | 0
331 | 00; | 0
332 | 00; | 0
333 | 00; | 0
334 | 00; | 0
335 | 00; | 0
336 | 00; | 0
337 | 00; | 0
338 | 00; | 0
339 | 00; | 0
33A | 00; | 0
33B | 00; | 0
33C | 00; | 0
33D | 00; | 0
33E | 00; | 0
33F | 00; | 0
340 | 00; | 0
341 | 00; | 0
342 | 00; | 0
343 | 00; | 0
344 | 00; | 0
345 | 00; | 0
346 | 00; | 0
347 | 00; | 0
348 | 00; | 0
349 | 00; | 0
34A | 00; | 0
34B | 00; | 0
34C | 00; | 0
34D | 00; | 0
34E | 00; | 0
34F | 00; | 0
350 | 00; | 0
351 | 00; | 0
352 | 00; | 0
353 | 00; | 0
354 | 00; | 0
355 | 00; | 0
356 | 00; | 0
357 | 00; | 0
358 | 00; | 0
359 | 00; | 0
35A | 00; | 0
35B | 00; | 0
35C | 00; | 0
35D | 00; | 0
35E | 00; | 0
35F | 00; | 0
360 | 00; | 0
361 | 00; | 0
362 | 00; | 0
363 | 00; | 0
364 | 00; | 0
365 | 00; | 0
366 | 00; | 0
367 | 00; | 0
368 | 00; | 0
369 | 00; | 0
36A | 00; | 0
36B | 00; | 0
36C | 00; | 0
36D | 00; | 0
36E | 00; | 0
36F | 00; | 0
370 | 00; | 0
371 | 00; | 0
372 | 00; | 0
373 | 00; | 0
374 | 00; | 0
375 | 00; | 0
376 | 00; | 0
377 | 00; | 0
378 | 00; | 0
379 | 00; | 0
37A | 00; | 0
37B | 00; | 0
37C | 00; | 0
37D | 00; | 0
37E | 00; | 0
37F | 00; | 0
380 | 00; | 0
381 | 00; | 0
382 | 00; | 0
383 | 00; | 0
384 | 00; | 0
385 | 00; | 0
386 | 00; | 0
387 | 00; | 0
388 | 00; | 0
389 | 00; | 0
38A | 00; | 0
38B | 00; | 0
38C | 00; | 0
38D | 00; | 0
38E | 00; | 0
38F | 00; | 0
390 | 00; | 0
391 | 00; | 0
392 | 00; | 0
393 | 00; | 0
394 | 00; | 0
395 | 00; | 0
396 | 00; | 0
397 | 00; | 0
398 | 00; | 0
399 | 00; | 0
39A | 00; | 0
39B | 00; | 0
39C | 00; | 0
39D | 00; | 0
39E | 00; | 0
39F | 00; | 0
3A0 | 00; | 0
3A1 | 00; | 0
3A2 | 00; | 0
3A3 | 00; | 0
3A4 | 00; | 0
3A5 | 00; | 0
3A6 | 00; | 0
3A7 | 00; | 0
3A8 | 00; | 0
3A9 | 00; | 0
3AA | 00; | 0
3AB | 00; | 0
3AC | 00; | 0
3AD | 00; | 0
3AE | 00; | 0
3AF | 00; | 0
3B0 | 00; | 0
3B1 | 00; | 0
3B2 | 00; | 0
3B3 | 00; | 0
3B4 | 00; | 0
3B5 | 00; | 0
3B6 | 00; | 0
3B7 | 00; | 0
3B8 | 00; | 0
3B9 | 00; | 0
3BA | 00; | 0
3BB | 00; | 0
3BC | 00; | 0
3BD | 00; | 0
3BE | 00; | 0
3BF | 00; | 0
3C0 | 00; | 0
3C1 | 00; | 0
3C2 | 00; | 0
3C3 | 00; | 0
3C4 | 00; | 0
3C5 | 00; | 0
3C6 | 00; | 0
3C7 | 00; | 0
3C8 | 00; | 0
3C9 | 00; | 0
3CA | 00; | 0
3CB | 00; | 0
3CC | 00; | 0
3CD | 00; | 0
3CE | 00; | 0
3CF | 00; | 0
3D0 | 00; | 0
3D1 | 00; | 0
3D2 | 00; | 0
3D3 | 00; | 0
3D4 | 00; | 0
3D5 | 00; | 0
3D6 | 00; | 0
3D7 | 00; | 0
3D8 | 00; | 0
3D9 | 00; | 0
3DA | 00; | 0
3DB | 00; | 0
3DC | 00; | 0
3DD | 00; | 0
3DE | 00; | 0
3DF | 00; | 0
3E0 | 00; | 0
3E1 | 00; | 0
3E2 | 00; | 0
3E3 | 00; | 0
3E4 | 00; | 0
3E5 | 00; | 0
3E6 | 00; | 0
3E7 | 00; | 0
3E8 | 00; | 0
3E9 | 00; | 0
3EA | 00; | 0
3EB | 00; | 0
3EC | 00; | 0
3ED | 00; | 0
3EE | 00; | 0
3EF | 00; | 0
3F0 | 00; | 0
3F1 | 00; | 0
3F2 | 00; | 0
3F3 | 00; | 0
3F4 | 00; | 0
3F5 | 00; | 0
3F6 | 00; | 0
3F7 | 00; | 0
3F8 | 00; | 0
3F9 | 00; | 0
3FA | 00; | 0
3FB | 00; | 0
3FC | 00; | 0
3FD | 00; | 0
3FE | 00; | 0
3FF | 00; | 0
400 | 00; | 0
401 | 00; | 0
402 | 00; | 0
403 | 00; | 0
404 | 00; | 0
405 | 00; | 0
406 | 00; | 0
407 | 00; | 0
408 | 00; | 0
409 | 00; | 0
40A | 00; | 0
40B | 00; | 0
40C | 00; | 0
40D | 00; | 0
40E | 00; | 0
40F | 00; | 0
410 | 00; | 0
411 | 00; | 0
412 | 00; | 0
413 | 00; | 0
414 | 00; | 0
415 | 00; | 0
416 | 00; | 0
417 | 00; | 0
418 | 00; | 0
419 | 00; | 0
41A | 00; | 0
41B | 00; | 0
41C | 00; | 0
41D | 00; | 0
41E | 00; | 0
41F | 00; | 0
420 | 00; | 0

## CustomVar4
Variable short name | Description for variable
80 | last_action
81 | fcu_filter
82 | PT100_7_water_return
83 | PT100_7_water_supply
84 | PT100_7_air_return
85 | PT100_7_air_supply

## ModbusVar4
Variable short name | Description for variable
0 | m_user
1 | m_workflow
2 | m_rcu_relays
3 | m_fcu_speed
4 | m_fcu_setpoint
5 | m_current_temp
6 | m_bell_ring
7 | m_PT100_7_water_return
8 | m_PT100_7_water_supply
9 | m_PT100_7_air_return
A | m_PT100_7_air_supply
B | m_notify | 0=restart 1=panelpress

## Calc
Tick from midnight
| HH |  | MM |  | SS |  | Tick | Hex
| 4 |  | 0 |  | 0
Tick | 144000000 |  | 0 |  | 0 | Tot: | 144000000 | 08 | 95 | 44 | 00
[7 empty] | 08954400 | Hex
| BIN |  | HEX |  | DEC
BIN2HEX | 100000 |  | 20
HEX2BIN | 1000 |  | 8 |  |  |  |  | 00449508
DEC2HEX |  |  | 4 |  | 4
HEX2DEC |  |  | A |  | 10
GSW Button Assignments
RegDec | RegHex | Hex Value High | Hex Value Low | Bin Value High | Bin Value Low | GS Button# | Button Color | GS2 | GS4 | GS6 | GS8 | GS10 | GS12
13 | 0D | 00 | 01 | 00000000 | 1 | 1 | Blue |  |  |  | Blue | Blue | Blue
13 | 0D | 00 | 02 | 00000000 | 10 | 1 | Red |  |  |  | Red | Red | Red
13 | 0D | 00 | 03 | 00000000 | 11 | 1 | Cyan |  |  |  | Cyan | Cyan | Cyan
13 | 0D | 00 | 04 | 00000000 | 100 | 2 | Blue |  |  |  |  | Blue | Blue
13 | 0D | 00 | 08 | 00000000 | 1000 | 2 | Red |  |  |  |  | Red | Red
13 | 0D | 00 | 0C | 00000000 | 1100 | 2 | Cyan |  |  |  |  | Cyan | Cyan
13 | 0D | 00 | 10 | 00000000 | 10000 | 3 | Blue |  |  |  | Blue | Blue | Blue
13 | 0D | 00 | 20 | 00000000 | 100000 | 3 | Red |  |  |  | Red | Red | Red
13 | 0D | 00 | 30 | 00000000 | 110000 | 3 | Cyan |  |  |  | Cyan | Cyan | Cyan
13 | 0D | 00 | 40 | 00000000 | 1000000 | 4 | Blue | Blue | Blue | Blue | Blue | Blue | Blue
13 | 0D | 00 | 80 | 00000000 | 10000000 | 4 | Red | Red | Red | Red | Red | Red | Red
13 | 0D | 00 | C0 | 00000000 | 11000000 | 4 | Cyan | Cyan | Cyan | Cyan | Cyan | Cyan | Cyan
13 | 0D | 01 | 00 | 1 | 00000000 | 5 | Blue |  |  | Blue |  | Blue | Blue
13 | 0D | 02 | 00 | 10 | 00000000 | 5 | Red |  |  | Red |  | Red | Red
13 | 0D | 03 | 00 | 11 | 00000000 | 5 | Cyan |  |  | Cyan |  | Cyan | Cyan
13 | 0D | 04 | 00 | 100 | 00000000 | 6 | Blue | Blue | Blue | Blue | Blue | Blue | Blue
13 | 0D | 08 | 00 | 1000 | 00000000 | 6 | Red | Red | Red | Red | Red | Red | Red
13 | 0D | 0C | 00 | 1100 | 00000000 | 6 | Cyan | Cyan | Cyan | Cyan | Cyan | Cyan | Cyan
13 | 0D | 10 | 00 | 10000 | 00000000 | 7 | Blue |  | Blue | Blue | Blue | Blue | Blue
13 | 0D | 20 | 00 | 100000 | 00000000 | 7 | Black |  | Black | Black | Black | Black | Black
13 | 0D | 30 | 00 | 110000 | 00000000 | 7 | Blue |  | Blue | Blue | Blue | Blue | Blue
13 | 0D | 40 | 00 | 1000000 | 00000000 | 8 | Blue |  |  | Blue |  | Blue | Blue
13 | 0D | 80 | 00 | 10000000 | 00000000 | 8 | Black |  |  | Black |  | Black | Black
13 | 0D | C0 | 00 | 11000000 | 00000000 | 8 | Blue |  |  | Blue |  | Blue | Blue
14 | 0E | 00 | 01 | 00000000 | 1 | 9 | Blue |  | Blue | Blue | Blue | Blue | Blue
14 | 0E | 00 | 02 | 00000000 | 10 | 9 | Black |  | Black | Black | Black | Black | Black
14 | 0E | 00 | 03 | 00000000 | 11 | 9 | Blue |  | Blue | Blue | Blue | Blue | Blue
14 | 0E | 00 | 04 | 00000000 | 100 | 10 | Blue |  |  |  | Blue | Blue | Blue
14 | 0E | 00 | 08 | 00000000 | 1000 | 10 | Black |  |  |  | Black | Black | Black
14 | 0E | 00 | 0C | 00000000 | 1100 | 10 | Blue |  |  |  | Blue | Blue | Blue
14 | 0E | 00 | 10 | 00000000 | 10000 | 11 | Blue |  |  |  |  | Blue | Blue
14 | 0E | 00 | 20 | 00000000 | 100000 | 11 | Black |  |  |  |  | Black | Black
14 | 0E | 00 | 30 | 00000000 | 110000 | 11 | Blue |  |  |  |  | Blue | Blue
14 | 0E | 00 | 40 | 00000000 | 1000000 | 12 | Blue |  |  |  | Blue |  | Blue
14 | 0E | 00 | 80 | 00000000 | 10000000 | 12 | Black |  |  |  | Black |  | Black
14 | 0E | 00 | C0 | 00000000 | 11000000 | 12 | Blue |  |  |  | Blue |  | Blue
REVERSE
RegDec | RegHex | Hex Value High | Hex Value Low | Bin Value High | Bin Value Low | GS Button# | Button Color | GS2 | GS4 | GS6 | GS8 | GS10 | GS12
13 | 0D | 00 | 01 | 00000000 | 1 | 1 | Blue |  |  |  | Blue | Blue | Blue
13 | 0D | 00 | 02 | 00000000 | 10 | 1 | Red |  |  |  | Red | Red | Red
13 | 0D | 00 | 03 | 00000000 | 11 | 1 | Cyan |  |  |  | Cyan | Cyan | Cyan
13 | 0D | 00 | 04 | 00000000 | 100 | 2 | Blue |  |  |  |  | Blue | Blue
13 | 0D | 00 | 08 | 00000000 | 1000 | 2 | Red |  |  |  |  | Red | Red
13 | 0D | 00 | 0C | 00000000 | 1100 | 2 | Cyan |  |  |  |  | Cyan | Cyan
13 | 0D | 00 | 10 | 00000000 | 10000 | 3 | Blue |  |  |  | Blue | Blue | Blue
13 | 0D | 00 | 20 | 00000000 | 100000 | 3 | Red |  |  |  | Red | Red | Red
13 | 0D | 00 | 30 | 00000000 | 110000 | 3 | Cyan |  |  |  | Cyan | Cyan | Cyan
13 | 0D | 00 | 40 | 00000000 | 1000000 | 4 | Blue | Blue | Blue | Blue | Blue | Blue | Blue
13 | 0D | 00 | 80 | 00000000 | 10000000 | 4 | Red | Red | Red | Red | Red | Red | Red
13 | 0D | 00 | C0 | 00000000 | 11000000 | 4 | Cyan | Cyan | Cyan | Cyan | Cyan | Cyan | Cyan
13 | 0D | 01 | 00 | 1 | 00000000 | 5 | Blue |  |  | Blue |  | Blue | Blue
13 | 0D | 02 | 00 | 10 | 00000000 | 5 | Red |  |  | Red |  | Red | Red
13 | 0D | 03 | 00 | 11 | 00000000 | 5 | Cyan |  |  | Cyan |  | Cyan | Cyan
13 | 0D | 04 | 00 | 100 | 00000000 | 6 | Blue | Blue | Blue | Blue | Blue | Blue | Blue
13 | 0D | 08 | 00 | 1000 | 00000000 | 6 | Red | Red | Red | Red | Red | Red | Red
13 | 0D | 0C | 00 | 1100 | 00000000 | 6 | Cyan | Cyan | Cyan | Cyan | Cyan | Cyan | Cyan
13 | 0D | 10 | 00 | 10000 | 00000000 | 7 | Blue |  | Blue | Blue | Blue | Blue | Blue
13 | 0D | 20 | 00 | 100000 | 00000000 | 7 | Black |  | Black | Black | Black | Black | Black
13 | 0D | 30 | 00 | 110000 | 00000000 | 7 | Blue |  | Blue | Blue | Blue | Blue | Blue
13 | 0D | 40 | 00 | 1000000 | 00000000 | 8 | Blue |  |  | Blue |  | Blue | Blue
13 | 0D | 80 | 00 | 10000000 | 00000000 | 8 | Black |  |  | Black |  | Black | Black
13 | 0D | C0 | 00 | 11000000 | 00000000 | 8 | Blue |  |  | Blue |  | Blue | Blue
14 | 0E | 00 | 01 | 00000000 | 1 | 9 | Blue |  | Blue | Blue | Blue | Blue | Blue
14 | 0E | 00 | 02 | 00000000 | 10 | 9 | Black |  | Black | Black | Black | Black | Black
14 | 0E | 00 | 03 | 00000000 | 11 | 9 | Blue |  | Blue | Blue | Blue | Blue | Blue
14 | 0E | 00 | 04 | 00000000 | 100 | 10 | Blue |  |  |  | Blue | Blue | Blue
14 | 0E | 00 | 08 | 00000000 | 1000 | 10 | Black |  |  |  | Black | Black | Black
14 | 0E | 00 | 0C | 00000000 | 1100 | 10 | Blue |  |  |  | Blue | Blue | Blue
14 | 0E | 00 | 10 | 00000000 | 10000 | 11 | Blue |  |  |  |  | Blue | Blue
14 | 0E | 00 | 20 | 00000000 | 100000 | 11 | Black |  |  |  |  | Black | Black
14 | 0E | 00 | 30 | 00000000 | 110000 | 11 | Blue |  |  |  |  | Blue | Blue
14 | 0E | 00 | 40 | 00000000 | 1000000 | 12 | Blue |  |  |  | Blue |  | Blue
14 | 0E | 00 | 80 | 00000000 | 10000000 | 12 | Black |  |  |  | Black |  | Black
14 | 0E | 00 | C0 | 00000000 | 11000000 | 12 | Blue |  |  |  | Blue |  | Blue
Blink Button to black for .5 seconds
| Entry | Here | bin 2 hex | bin 2 hex | FILTER | GS1 | GS2 | GS3
| 11111111 | 11111100 | FF | FC | btn 1
| 11111111 | 11110011 | FF | F3 | btn 2
| 11111111 | 11001111 | FF | CF | btn 3
| 1010110 | 01010101 | 56 | 55 | btn 4 | x | x | x
| 11111100 | 11111111 | FC | FF | btn 5
| 11110011 | 11111111 | F3 | FF | btn 6 | x | x | x
| 11001111 | 11111111 | CF | FF | btn 7 | x |  | x
| 00111111 | 11111111 | 3F | FF | btn 8
| 11111111 | 11111100 | FF | FC | btn 9 | x |  | x
| 11111111 | 11110011 | FF | F3 | btn 10 |  |  |  |  | 10101010 | aa
| 11111111 | 11001111 | FF | CF | btn 11
| 11111111 | 00111111 | FF | 3F | btn 12

## MemoryVar
|  | Backupped variables |  |  |  | Start | Len | Desc | Volatile variables
0 | 0 | 0xe0084000 | MUR |  |  | Card event log |  |  | 0x7fe00000-0x7fe001ff | Event last status bitmap
1 | 1 | 0xe0084004 | DND |  | Log | 0xe0084600 | 0x200 | 64 events | #define VOLV_BmEve ((unsigned char *)0x7fe00000)
2 | 2 | 0xe0084008 | Call |  | Revoked cards | 0xe0084500 | 0x100 | 64 Ids (32bit crc) | #define VOLV_CardInTig | ((unsigned int *)0x7fe00200)
3 | 3 | 0xe008400C | SOS | [5 empty] | #define VOLV_free1 ((unsigned int *)0x7fe00204)
4 | 4 | 0xe0084010 | Laundry |  |  | __top_RAM_RTC_2 = 0xe0084000 + 0x800; |  |  | #define VOLV_free2 ((unsigned char *)0x7fe00208)
5 | 5 | 0xe0084014 | Master On/Off | [5 empty] | #define VOLV_free3 ((unsigned char *)0x7fe0020C)
6 | 6 | 0xe0084018 | Tag1 status | [5 empty] | #define VOLV_LastThDev *((unsigned int *)0x7fe00210)
7 | 7 | 0xe008401C | Tag2 status | [5 empty] | #define VOLV_LastThTemp *((unsigned int *)0x7fe00214)
8 | 8 | 0xe0084020 | Tag3 status | [5 empty] | #define VOLV_LastThComp *((unsigned int *)0x7fe00218) |  | // Card role/presence
9 | 9 | 0xe0084024 | Tag4 status | [5 empty] | #define VOLV_LastThOff *((unsigned int *)0x7fe0021C)
10 | A | 0xe0084028 | Tag5 status | [5 empty] | #define VOLV_LastCardChk ((unsigned int *)0x7fe00220)
11 | B | 0xe008402C | Tag6 status | [5 empty] | #define VOLV_LastCard ((unsigned char *)0x7fe00224)
12 | C | 0xe0084030 | Tag1 guest temp | in decimals |  |  |  |  | #define VOLV_WindowContacts ((unsigned char *)0x7fe00240)
13 | D | 0xe0084034 | Tag2 guest temp | in decimals
14 | E | 0xe0084038 | Tag3 guest temp | in decimals |  |  |  |  | Last TAG Out Set (proxy)
15 | F | 0xe008403C | Tag4 guest temp | in decimals
16 | 10 | 0xe0084040 | Tag5 guest temp | in decimals
17 | 11 | 0xe0084044 | Tag6 guest temp | in decimals |  |  |  |  | 0x7fe00400 | VOLV_ProgramVariable
18 | 12 | 0xe0084048 | Winter/Summer | 0=NOP, 1=Summer. 2=Winter
19 | 13 | 0xe008404C | Intervention offset | in decimals
20 | 14 | 0xe0084050 | Room empty temperature in decimal
(if bit 15 0x8000 ON, value is added to offset)
21 | 15 | 0xe0084054 | User presence/role
22 | 16 | 0xe0084058 | MuR Workflow status
23 | 17 | 0xe008405c | GSW1
24 | 18 | 0xe0084060 | GSW2
25 | 19 | 0xe0084064 | GSW3
26 | 1A | 0xe0084068 | GSW4
27 | 1B | 0xe008406c | GSW5
28 | 1C | 0xe0084070 | GSW6
29 | 1D | 0xe0084074 | GSW7
30 | 1E | 0xe0084078 | GSW8
31 | 1F | 0xe008407c | GSW9
32 | 20 | 0xe0084080 | GSW10
33 | 21 | 0xe0084084 | IOEXP1 proxy
34 | 22 | 0xe0084088 | IOEXP2 proxy
35 | 23 | 0xe008408c | IOEXP3 proxy
36 | 24 | 0xe0084090 | IOEXP4 proxy
37 | 25 | 0xe0084094 | IOEXP5 proxy
38 | 26 | 0xe0084098 | IOEXP6 proxy