## How To Fill
HOW TO FILL
Device Type | GS12 | GS9 | GS6 | GSTA/GSTA2 | TAG/TAG2
Device Configuration (Identifies Button Location and Applicable colors - Blue and White are interchangeable)
Valid Keywords |  |  | Keyword definition
For Relays | On, Off, On/Off, On for x sec, On after x Sec, Off after x sec |  | On/Off - Toggle On/Off
For Dimmers | 100%, 0%, 100%/0%,'Y%, Y% for x sec, Y% after x sec |  | On - Set to On
| (In case of defining only "Y%", |  | Off - Set to Off
| a single quote should be included in the cell before |  | On for x sec - Sets relay to on for x sec and then off
| defining the % value) |  | On after x sec - Sets relay to On after x sec and remains on
Off for x sec - Sets relay Off for x sec and then turn on again
Y% - Sets dimmer to Y%. Note, Y% may not correlate to luminostiy to Y%. It will only set channel output to Y%
Notes: | All Inputs are defined in Row 13 & 14
All outputs nodes to be defined in column G
For functions that are part of Scene, function name should include "Scene" Terminology
For a button which Needs Scene toggle or Scene Cycle - the function should be split into x number of columns each representing scene function. Sequence of Functionality would define automatically the button press sequence
Single Button Curtain Open/Close/Stop should be indicated in 2 or 3 columns as applicable
EOL Row and Column to be clearly mentioned
it's not allowed to add rows above Row 15 or before Column J
Prioroty of Output Modules (Defines the sequence of module population on CFS)
1. RCU
2. IOEXP with FCU connected
3. IOEXP with Digital Inputs used
4. Any other IOEXP/IODEXPs
FCU Control Rows should be banded in single color representing each FCU
Row 13: should only have device name or input ID. Function name to be filled in Row 14
Leaving a cell Blank makes no valid action. For scenes requiring to turn off the circuit - mention explicitly to turn off
All columns should have a unique input defined. Duplication of Inputs to RCU is not acceptable
All unique functions should be uniquely named. Example: if Entrance has master and bedside has master, do not name both inputs as "Master". Should be "Entrance Master" and "Bedside Master"
In case of integrations where entry points/register is used, add a new sheet where all the mapping is captured

## Global Parameters
# | Global Parameters | Primary | Optional Addon Information | Explanations
1 | Occupancy
A | Exit Timeout - Guest | 15 |  | Define in minutes (For Multistage exits, define each timeout seperated by "+" symbol)
B | Exit Timeout - Staff | 5 |  | Define in minutes
C | Exit Timeout - Commissioning Mode | 2 |  | Define in minutes
D | Occupancy Based On | Motion with Door Contact |  | - Keycard; Motion; Motion & Keycard; Always Occupied, Check-in/Check-out
E | Door Lock Integration | Not Applicable(Door Contact) | 4 | - Not applicable, Vingcard, Hafele, Salto, Kaba
F | Property Timezone | UTC+10:00 (Brisbane) |  | - Select the property timezone in UTC+/-XX
G | Panel Accessibilty by Staff | Yes - For All |  | Default - Not Accessible
2 | IDPG
A | Door Bell | RL | RCU, RL12 | Select Location of Bell. Define RL or GP Device ID
B | Privacy (DND) | Glass Panel |  | Identify addressed from Relay or Glass Panel(Relay Position: for RCU - RL x, for expansion: Bus 2,ID64,RL x
C | Service (MUR) | Glass Panel |  | Identify addressed from Relay or Glass Panel(Relay Position: for RCU - RL x, for expansion: Bus 2,ID64,RL x
D | Room Number Brightness | 60% |  | Define in %age - Default 60%
E | Icons Brightness | 60% |  | Define in %age - Default 60%
3 | TAG
A | Display Temperature | Rounded |  | Default - Absolute (Displayed as: 23.2⁰); Rounded Off (Displayed as: 23⁰C)
B | Incr/Decr. Steps | Steps of 1 |  | Default - Steps of 1C, Alternate - 0.5C. F is always steps of 1F
C | Non Interactive Mode
i | Display & Icons | None |  | Display Current Temp, Setpoint, Turn off display
ii | Icons Brightness | 30% |  | Define in %age - Default 0%
iii | Display Brightness | 30% |  | Define in %age - Default 10%
D | Interactive Mode
i | Display | Setpoint |  | Display Current Temp, Setpoint
ii | Icons Brightness | 60% |  | Define in %age - Default 80%
iii | Display Brightness | 60% |  | Define in %age - Default 80%
iv | Non-Interactive to Interactive transition | Wake Panel & Execute Function for Fan Only |  | Default - Wake Panel and Execute Function Wake Panel and Execute Function for Fan Only - 1st Press of temp Wakes Panel, 2nd Press onwards functions are executed. For Fan Speed, directly executes Wake Panel Only - 1st Press Wakes Panel, 2nd Press onwards functions are executed
E | Window Contact Status | Show Open, Go To Sleep |  | - Show open, never sleep: When WC opens, t-stat display shows text "open" and display stays even in non-interactive mode - Show open, Go to sleep: in this case When WC opens, t-stat display shows text "open" and after timeout display goes off. when pressing button goes back to show Open - default - No Feedback, T-stat Blocked - Doesn’t shows any text feedback, just blocks TAG with Off Icon lit up, if off is independant icon on GSTA/TAG design - Not Applicbale: No window contact in the project
F | Intervention Offset |  |  | Defines the deadband in order to maintain the temp range in a band of +/- defined temperature below reference to the selected setpoint
i | Rented - Occupied | 0.3 |  | Define in ⁰C
ii | Rented - Unoccupied | 2.5 |  | Define in ⁰C
ii | Vacant - Occupied | 2.5 |  | Define in ⁰C
iv | Vacant - Unoccupied | 5 |  | Define in ⁰C
G | Hysterisis Offset |  |  | Defines the deadband in order to avoid frequent switchover between heating/cooling operatations
i | Occupied | 0.3 |  | Define in ⁰C
ii | Not Occupued | 0.3 |  | Define in ⁰C
H | Room Empty Temperature | Relative | 0 | Preset: Predefined Temperature in ⁰C. Relative: ±x ⁰C. Example Use cases for Relative: Guest setpoint = 24C, mode = cooling. Upon guest absence, target temp = 24+x C Guest setpoint = 24C, mode = heating. Upon guest absence, target temp = 24-x C defining x=0 means, the guest setpoint is maintanined even in non-occupancy
I | Room Empty Fan Speed | Auto
I | Room Empty Season | Auto
J | Min Fan Speed | No
K | Startup Display Temp in | ⁰C |  | Display on Startup shows temp in ⁰C or ⁰F
L | Safe Startup Set Temperature | 24 |  | Define in ⁰C…Appllicable if no server or server events aren't coming in through
M | Safe Startup Fan Speed | Auto |  | Appllicable if no server or server events aren't coming in through
N | Safe Startup Season | Auto |  | Appllicable if no server or server events aren't coming in through
O | Safe Intervention Offset | 0.5 |  | Default Values on Startup
P | Safe Hysterisis Offset | 0.5 |  | Default Values on Startup
Q | Min Allowed Set Temperature | 18 |  | Define in ⁰C
R | Max Allowed Set Temperature | 28 |  | Define in ⁰C
S | Over Heating Setpoint | 35 |  | Define in ⁰C
T | Anti Icing Setpoint | 5 |  | Define in ⁰C
U | Floating actuator - cooling | 75 |  | Define in sec
V | Floating actuator - heating | 75 |  | Define in sec
W | Proximity feature | Disable |  | Applicable for Flat 2.0 panels only
X | Audible feedback feature | Enable |  | Applicable for Flat 2.0 panels only
4 | GSW
A | Non Interactive Mode
i | Icon Feedback | Default - Sleep Mode |  | Default - Sleep Mode (All icons off, except guest service feedbacks)
ii | Icons Brightness | 15% |  | Define in %age
B | Interactive Mode
i | Icon Feedback | All On |  | Default - All on
ii | Icons Brightness | 60% |  | Define in %age
C | Proximity feature | Disable |  | Applicable for Flat 2.0 panels only
D | Audible feedback feature | Enable |  | Applicable for Flat 2.0 panels only
5 | Enable Server Notification for:
A | TCP Com Port | Ethernet |  | Default Ethernet. Other option: Wifi Antenna on Bus 3, Wifi Antenna on Bus 4
B | Custom | No |  | Applicable only if Feature Present
6 | Server Managed Parameters
A | Check in Guest Setpoint @ t=0 | 22 |  | Customer Setpoint to the room after guest check-in. Effective when room is occupied
B | Check in User Fan Speed @ t=0 | Auto |  | Customer Fan Speed for the room after guest check-in. Effective when room is occupied
C | Check in Room Empty Set point @ t=0 | 24 |  | Customer Setpoint to the room after guest check-in. Effective when room is not-occupied
D | Check in Room Empty Set point @ t>=60 | 24 |  | Customer Setpoint to the room 60 mins after guest check-in. Effective when room is not-occupied
E | Duration Welcome Maintenance @ t=60 | 60 |  | Fixed Timeout
F | Check in Room Empty Fan Speed @ t=0 | Auto |  | Customer Fan Speed for the room after guest check-in. Effective when room is not-occupied
G | Check out User Set point | Delta 0 |  | Customer Setpoint to the room after guest check-out. Effective when room is occupied
H | Check out User Fan Speed | Auto |  | Customer Fan Speed for the room after guest check-out. Effective when room is occupied
I | Check out Room Empty Set Point | Delta 0 |  | Customer Setpoint to the room after guest check-out. Effective when room is not-occupied
J | Check out Room Empty Fan Speed | Auto |  | Customer Fan Speed for the room after guest check-out. Effective when room is not-occupied
K | Season Mode | Auto |  | Season Mode - Applied to All rooms irrespective of Checked in or checked out
L | API Entry Points needed? | No |  | Define if Entry points needed for API (mobile app, request management, etc.) if Set to Yes, please populate a new TAB with details of all relvant entry points
Note on D7: SCH: Define Bus Number here

## Local Functions
|  |  |  | Control Function sheet |  |  |  | Rev 0 | [5 empty] | PIR : e008 4208 | [19 empty] | Insert Graphic |  |  | Insert Graphic |  |  |  | Insert Graphic |  |  |  |  | Insert Graphic | [8 empty] | Insert Graphic | [5 empty] | Insert Graphic | [5 empty] | Insert Graphic | [10 empty] | Insert Graphic
|  |  |  | Room Type |  | Standard Room |  | SK1 | [5 empty] | Last action : e008 4200
|  |  |  | Project Name |  | Project 1 | [7 empty] | Commissioing mode : e008 4240 set 1: exit in commissioning mode timeout set 0: exit in default timeout
|  |  |  | Date of Last Update |  | 2020-10-30
General Notes:
RCU Domain | [7 empty] | Bus | [5 empty] | RCU1 |  |  |  | RCU1 | [7 empty] | RCU1 |  |  |  | RCU1 |  |  |  | RCU1 |  |  | RCU1 |  |  |  | RCU1 |  |  |  |  | RCU1 | [8 empty] | RCU1 | [5 empty] | RCU1 | [5 empty] | RCU1 | [10 empty] | RCU1 | [8 empty] | EOL
Device Type | [13 empty] | DC |  |  |  | RCU | [7 empty] | IOEXP1 |  |  |  | IOEXP2 |  |  |  | IDPG |  |  | GS6 |  |  |  | GS6 |  |  |  |  | TAG1 | [8 empty] | GS9 | [5 empty] | GS6 | [5 empty] | GS12 | [10 empty] | GS9 | [8 empty] | EOL
Bus | [7 empty] | Bus | [5 empty] | 4 | [11 empty] | 2 |  |  |  | 2 |  |  |  | 1 |  |  | 1 |  |  |  | 1 |  |  |  |  | 1 | [8 empty] | 3 | [5 empty] | 3 | [5 empty] | 3 | [10 empty] | 3 | [8 empty] | EOL
ID | [7 empty] | ID | [5 empty] | 70 | [11 empty] | 64 |  |  |  | 65 |  |  |  | 0A |  |  | 28 |  |  |  | 29 |  |  |  |  | 1E | [8 empty] | 28 | [5 empty] | 29 | [5 empty] | 2A | [10 empty] | 2B | [8 empty] | EOL
Input Number | [17 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1-4 | 1-4 | 6 | 1 | 3 | 4 | 6 | 1 | 3 | 4 | 5 | 6 | 2 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 1 | 2 | 3 | 4 | 5 | 6 | 1 | 2 | 3 | 4 | 5 | 6 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
Commit Change against Prev Version
|  |  | Module | Output Ref | RCU Bus | Circuit | Eval Entries | Circuit Type |  | PMS/BMS - Server Triggered |  |  |  | Occupancy |  |  |  | In 1 | In 2 | In 3 | In 4 | In 5 | In 6 | In 7 | In 8 | In 1 | In 2 | In 3 | In 4 | In 1 | In 2 | In 3 | In 4 | CORRIDOR PANEL |  |  | ENTRY PANEL |  |  |  | BATHROOM PANEL |  |  |  |  | THERMOSTAT PANEL | [8 empty] | BEDSIDE LEFT | [5 empty] | BEDSIDE RIGHT | [5 empty] | ENTRANCE BEDROOM | [10 empty] | PANTRY
[9 empty] | Start-up | Check-in Scene | Check-out Scene | BMS - Trig 1 | BMS - Trig 2 | Guest Welcome Scene | Guest Subs. Entry Scene | Staff Entry Scene | Exit Scene | Door Contact | Motion Sensor - Bathroom | Shower Light | Vanity Light | Corridor Light | Spare | Spare | Balcony Contact | Spare | Spare | Study Lamp | Spare | Balcony Uplight | Balcony Wall light | Balcony Master | Spare | PRIVACY | SERVICE | DOOR BELL | PRIVACY | MASTER | SERVICE | ENTRANCE | PRIVACY | BATH BRIGHT SCENE | BATH RELAX SCENE | Motion Sensor | BATH ALL OFF SCENE | C/F | Temp - | Temp + | Fan Low | Fan Med | Fan High | Off | Motion Sensor | Auto | Bedside Lamp Left | Bedroom Master | Bedroom Bright Scene | Reading Lamp Left | Bedroom Relax Scene | Night Scene | Bedroom Bright Scene | Bedroom Master | Bedside Lamp Right | Night Scene | Bedroom Relax Scene | Reading Lamp Right | PRIVACY | Bedroom Master | SERVICE | Night Scene | Bedroom Relax Scene | Bedroom Entrance Light Right | Bedside Lamp Right | Bedside Lamp Left | Reading Lamp Right | Motion Sensor | Reading Lamp Left | PRIVACY | Bedroom Master | Bedroom Entrance Light Left | Night Scene | Bedroom Relax Scene | Bedroom Entrance Light Right | Bedside Lamp Right | Bedside Lamp Left | Pantry Light
Function Related Comments -> | [16 empty] | Timeout = 15 mins
Test Status (OK/Not OK) ->
RCU-A3A01 |  | 1 | RCU-A3A01 | RL-1 | N/A | Room Load Contactor |  | On/Off | [5 empty] | Off | Off | Off | On | In 2: Used for Occupancy | DND Enabled. Icon Lights up in red | MUR Enabled Icon Lights up in green |  | Enables DND Corridor Panel Lights up in Red Door Bell Muted |  | Enables MUR Corridor Panel Lights up in Green Door Bell Enabled |  | Enables DND Corridor Panel Lights up in Red Door Bell Muted | [25 empty] | Enables DND Corridor Panel Lights up in Red Door Bell Muted |  | Enables MUR Corridor Panel Lights up in Green Door Bell Enabled | [8 empty] | Enables DND Corridor Panel Lights up in Red Door Bell Muted
|  | 2 | RCU-A3A01 | RL-2 | N/A | Entry Down Light |  | On/Off | [5 empty] | On | Last Status | On | Off | [20 empty] | On/Off |  | On/Off | [15 empty] | On/Off |  |  |  | Off |  | On/Off |  | Off |  |  |  | On/Off |  | Off | [8 empty] | On/Off | On/Off | Off
|  | 3 | RCU-A3A01 | RL-3 | N/A | Entry Wall Lamp |  | On/Off | [5 empty] | On | Last Status | On | Off | In 5: On/Off |  |  |  |  | On/Off |  | On/Off | [15 empty] | On/Off | On |  |  | Off | On | On/Off |  | Off |  |  |  | On/Off |  | Off | [8 empty] | On/Off | On/Off | Off
|  | 4 | RCU-A3A01 | RL-4 | N/A | Bathroom Down Light |  | On/Off | [6 empty] | Last Status | On | Off | [20 empty] | On/Off |  |  |  | On |  |  | Off | [14 empty] | Off |  |  |  | Off | [5 empty] | Off | [10 empty] | Off
|  | 5 | RCU-A3A01 | RL-5 | N/A | Shower Down Light |  | On/Off | [6 empty] | Last Status | On | Off | In 3: On/Off |  |  |  |  | On/Off |  |  |  | On |  |  | Off | [14 empty] | Off |  |  |  | Off | [5 empty] | Off | [10 empty] | Off
|  | 6 | RCU-A3A01 | RL-6 | N/A | Vanity Light |  | On/Off | [6 empty] | Last Status | On | Off | In 4: On/Off |  |  |  |  | On/Off |  |  |  |  | On |  | Off | [14 empty] | Off |  |  |  | Off | [5 empty] | Off | [10 empty] | Off
|  | 7 | RCU-A3A01 | RL-7 | N/A | Bathroom Cove Light |  | On/Off | [6 empty] | Last Status | On | Off | [20 empty] | On/Off |  |  |  | On |  |  | Off | [14 empty] | Off |  |  |  | Off | [5 empty] | Off | [10 empty] | Off
|  | 8 | RCU-A3A01 | RL-8 | N/A | Bathroom Undercabinet Light |  | On/Off | [6 empty] | Last Status | On | Off | [20 empty] | On/Off |  |  |  |  | On |  | Off | [14 empty] | On |  |  |  | On | [5 empty] | On | [10 empty] | On
|  | 9 | RCU-A3A01 | RL-9 | N/A | Minibar Light |  | On/Off | [5 empty] | On | Last Status | On | Off | [20 empty] | On/Off | [17 empty] | On/Off | On |  | Off | On | On | On/Off |  | On | Off |  |  | On/Off |  | On | Off | On/Off | [6 empty] | On/Off |  | On | Off | On/Off
|  | 10 | RCU-A3A01 | RL-10 | N/A | Wardrobe Light |  | On/Off | [6 empty] | Last Status | On | Off | [20 empty] | On/Off | [17 empty] | On/Off | On |  | Off | Off | On | On/Off |  | Off | Off |  |  | On/Off |  | Off | Off | On/Off | [6 empty] | On/Off |  | Off | Off | On/Off
|  | 11 | RCU-A3A01 | RL-11 | N/A | Floor Lamp |  | On/Off | [5 empty] | On | Last Status | On | Off | [20 empty] | On/Off | [17 empty] | On/Off | On |  | On | Off | On | On/Off |  | Off | On |  |  | On/Off |  | Off | On | On/Off | [6 empty] | On/Off |  | Off | On | On/Off
|  | 12 | RCU-A3A01 | RL-12 | N/A | Door Bell |  | On/Off | [5 empty] | On | Last Status | On | Off | [18 empty] | On for 0.5s |  | On/Off
|  | 13 | RCU-A3A01 | RL-13 | N/A | Bedside Left Lamp |  | On/Off | [6 empty] | Last Status | On | Off | [20 empty] | On/Off | [16 empty] | On/off | On/Off |  |  | Off | Off |  | On/Off |  | Off | Off |  |  | On/Off |  | Off | Off |  |  | On/off |  |  |  |  | On/Off |  | Off | Off |  |  | On/off | On/Off
|  | 14 | RCU-A3A01 | RL-14 | N/A | Bedside Right Lamp |  | On/Off | [6 empty] | Last Status | On | Off | [20 empty] | On/Off | [17 empty] | On/Off |  |  | Off | Off |  | On/Off | On/Off | Off | Off |  |  | On/Off |  | Off | Off |  | On/Off | [5 empty] | On/Off | On/Off | Off | Off |  | On/Off |  | On/Off
|  | 15 | RCU-A3A01 | RL-15 | N/A | Reading Left |  | On/Off | [6 empty] | Last Status | On | Off | [20 empty] | On/Off | [17 empty] | On/Off |  | On/Off | Off | Off |  | On/Off |  | Off | Off |  |  | On/Off |  | Off | Off | [5 empty] | On/Off |  | On/Off |  | Off | Off |  |  |  | On/Off
|  | 16 | RCU-A3A01 | RL-16 | N/A | Reading Right |  | On/Off | [6 empty] | Last Status | On | Off | [20 empty] | On/Off | [17 empty] | On/Off |  |  | Off | Off |  | On/Off |  | Off | Off | On/Off |  | On/Off |  | Off | Off |  |  |  | On/Off |  |  |  | On/Off |  | Off | Off |  |  |  | On/Off
|  | 17 | RCU-A3A01 | AOUT-1 | N/A | Bedroom Cove |  | 0-10Vdc | [6 empty] | Last Status | 100% | 0% | [38 empty] | 0%/100% | 100% |  | 25% | 0% | 100% | 0%/100% |  | 0% | 25% |  |  | 0%/100% |  | 0% | 25% | [7 empty] | 0%/100% |  | 0% | 25%
|  | 18 | RCU-A3A01 | AOUT-2 | N/A | Spare |  | 0-10Vdc
IOEXP 1 | IOEXP-B02A ID: 64 | 1 | IOEXP-B02A | RL-1 | Bus 2 | Spare |  | On/Off
|  | 2 | IOEXP-B02A | RL-2 | Bus 2 | Spare |  | On/Off
|  | 3 | IOEXP-B02A | RL-3 | Bus 2 | Spare |  | On/Off
|  | 4 | IOEXP-B02A | RL-4 | Bus 2 | FCU - Cooling open |  | On/Off | [9 empty] | In 8: Off | [12 empty] | Toggle Display in C/F | Reduce Setpoint by 1C | Increase Setpoint by 1C | Based on Delta |  |  | Off |  | Based on Delta
|  | 5 | IOEXP-B02A | RL-5 | Bus 2 | FCU - Cooling close |  | On/Off | [40 empty] | Based on Delta
|  | 6 | IOEXP-B02A | RL-6 | Bus 2 | Study Light |  | On/Off | [6 empty] | Last Status | On | Off | In 3: On/Off |  |  |  |  | On/Off | [17 empty] | On/Off |  |  | Off | Off |  | On/Off |  | Off | Off |  |  | On/Off |  | Off | Off | [7 empty] | On/Off |  | Off | Off
|  | 17 | IOEXP-B02A | AOUT-1 | Bus 2 | Spare |  | 0-10Vdc
|  | 18 | IOEXP-B02A | AOUT-2 | Bus 2 | FCU - Variable Fan |  | 0-10Vdc | [9 empty] | In 8: Off | [12 empty] | Toggle Display in C/F | Reduce Setpoint by 1C | Increase Setpoint by 1C | 30% | 60% | 100% | Off |  | Based on Delta
IOEXP 2 | IOEXP-B02A ID: 65 | 1 | IOEXP-B02A | RL-1 | Bus 2 | Bedroom Downlight |  | On/Off | [6 empty] | Last Status | On | Off | [20 empty] | On/Off | [17 empty] | On/Off | On |  | Off | Off | On | On/Off |  | Off | Off |  |  | On/Off |  | Off | Off | [7 empty] | On/Off |  | Off | Off |  |  |  | On/Off
|  | 2 | IOEXP-B02A | RL-2 | Bus 2 | Bedroom Strip Light |  | On/Off | [6 empty] | Last Status | On | Off | [20 empty] | On/Off | [17 empty] | On/Off | On |  | On | Off | On | On/Off |  | Off | On |  |  | On/Off |  | Off | On | [7 empty] | On/Off |  | Off | On |  |  |  | On/Off
|  | 3 | IOEXP-B02A | RL-3 | Bus 2 | Headboard Light |  | On/Off | [5 empty] | On | Last Status | On | Off | [20 empty] | On/Off | [17 empty] | On/Off | On |  | Off | On | On | On/Off |  | On | Off |  |  | On/Off |  | On | Off | [7 empty] | On/Off |  | On | Off |  |  |  | On/Off
|  | 4 | IOEXP-B02A | RL-4 | Bus 2 | Balcony Wall Light |  | On/Off | [6 empty] | Last Status | On | Off | In 2: On/Off; In 3: On/Off |  |  |  |  | On/Off
|  | 5 | IOEXP-B02A | RL-5 | Bus 2 | Balcony Uplight |  | On/Off | [6 empty] | Last Status | On | Off | In 1: On/Off; In 3: On/Off |  |  |  |  | On/Off
|  | 6 | IOEXP-B02A | RL-6 | Bus 2 | Room Load Contactor |  | On/Off | [5 empty] | Off
|  | 17 | IOEXP-B02A | AOUT-1 | Bus 2 | Spare |  | 0-10Vdc
|  | 18 | IOEXP-B02A | AOUT-2 | Bus 2 | Study Cove |  | 0-10Vdc | [6 empty] | Last Status | 100% | 0% | [38 empty] | 0%/100% | 100% |  | 50% | 0% | 100% | 0%/100% |  | 0% | 50% |  |  | 0%/100% |  | 0% | 50% | [7 empty] | 0%/100% |  | 0% | 50%
IOEXP 3 | IOEXP-B02A ID: 66 | 1 | IOEXP-B02A | RL-1 | Bus 2 | Bedroom Entrance |  | On/Off | [6 empty] | Last Status | On | Off | [20 empty] | On/Off | [17 empty] | On/Off | On |  | Off | Off | On | On/Off |  | Off | Off |  |  | On/Off |  | Off | Off | [7 empty] | On/Off |  | Off | Off |  |  |  | On/Off
|  | 2 | IOEXP-B02A | RL-2 | Bus 2 | Bedroom Entrance Strip Light |  | On/Off | [6 empty] | Last Status | On | Off | [20 empty] | On/Off | [17 empty] | On/Off | On |  | Off | Off | On | On/Off |  | Off | Off |  |  | On/Off |  | Off | Off | [7 empty] | On/Off |  | Off | Off |  |  |  | On/Off
|  | 3 | IOEXP-B02A | RL-3 | Bus 2 | Spare |  | On/Off
|  | 4 | IOEXP-B02A | RL-4 | Bus 2 | Spare |  | On/Off
|  | 5 | IOEXP-B02A | RL-5 | Bus 2 | Room Load Contactor |  | On/Off | [5 empty] | On
|  | 6 | IOEXP-B02A | RL-6 | Bus 2 | Room Load Contactor |  | On/Off | [5 empty] | Off
|  | 17 | IOEXP-B02A | AOUT-1 | Bus 2 | Spare |  | 0-10Vdc
|  | 18 | IOEXP-B02A | AOUT-2 | Bus 2 | SPare |  | 0-10Vdc
IODEXP 1 | IODEXP-A04 ID: 6E | 1 | IODEXP-A04 | CH-1 | Bus 2 | Bedroom Entrance Dim |  | 0-10Vdc | [6 empty] | Last Status | 100% | 0% | [38 empty] | 0%/100% | 100% |  | 50% | 0% | 100% | 0%/100% |  | 0% | 50% |  |  | 0%/100% |  | 0% | 50% | [7 empty] | 0%/100% |  | 0% | 50%
|  | 2 | IODEXP-A04 | CH-2 | Bus 2 | Bedroom Entrance Strip Light Dim |  | 0-10Vdc | [6 empty] | Last Status | 100% | 0% | [38 empty] | 0%/100% | 100% |  | 50% | 0% | 100% | 0%/100% |  | 0% | 50% |  |  | 0%/100% |  | 0% | 50% | [7 empty] | 0%/100% |  | 0% | 50%
|  | 3 | IODEXP-A04 | CH-3 | Bus 2 | Spare |  | 0-10Vdc
|  | 4 | IODEXP-A04 | CH-4 | Bus 2 | Spare |  | 0-10Vdc
|  | 5 | IODEXP-A04 | CH-5 | Bus 2 | Spare |  | 0-10Vdc
|  | 6 | IODEXP-A04 | CH-6 | Bus 2 | Spare |  | 0-10Vdc
|  |  |  | BallastID |  |  |  | GroupID
DALI 1 | DALI-A01 ID: 32 | 1 | DALI A01 -1 | 1 | Bus 2 | Vanity Cove Light |  | 0 | [6 empty] | Last Status | 100% | 0% | [38 empty] | 0%/100% | 100% |  | 50% | 0% | 100% | 0%/100% |  | 0% | 50% |  |  | 0%/100% |  | 0% | 50% | [7 empty] | 0%/100% |  | 0% | 50%
|  | 2 | DALI A01 -1 | 2 | Bus 2 | Shower Light |  | 0 | [6 empty] | Last Status | 100% | 0% | In 3: 0%/100% | [22 empty] | 0%/100% | 100% |  | 50% | 0% | 100% | 0%/100% |  | 0% | 50% |  |  | 0%/100% |  | 0% | 50% | [7 empty] | 0%/100% |  | 0% | 50%
|  | 3 | DALI A01 -1 | 3 | Bus 2 | Vanity Light |  | 0,1 | [6 empty] | Last Status | 100% | 0% | In 3: 0%/100%; In 4: 0%/100% | [22 empty] | 0%/100% | 100% |  | 50% | 0% | 100% | 0%/100% |  | 0% | 50% |  |  | 0%/100% |  | 0% | 50% | [7 empty] | 0%/100% |  | 0% | 50%
|  | 4 | DALI A01 -1 | 4 | Bus 2 | Balcony Wall Light |  | 0,1 | [6 empty] | Last Status | 100% | 0% | [38 empty] | 0%/100% | 100% |  | 50% | 0% | 100% | 0%/100% |  | 0% | 50% |  |  | 0%/100% |  | 0% | 50% | [7 empty] | 0%/100% |  | 0% | 50%
|  | 5 | DALI A01 -2 | 1 | Bus 2 | Balcony Uplight |  | 0 | [6 empty] | Last Status | 100% | 0% | [38 empty] | 0%/100% | 100% |  | 50% | 0% | 100% | 0%/100% |  | 0% | 50% |  |  | 0%/100% |  | 0% | 50% | [7 empty] | 0%/100% |  | 0% | 50%
|  | 6 | DALI A01 -2 | 2 | Bus 2 | Balcony left |  | 0 | [6 empty] | Last Status | 100% | 0%
|  | 7 | DALI A01 -2 | 3 | Bus 2 | Balcony right |  | 0
|  | 8 | DALI A01 -2 | 4 | Bus 2 | Balcony middle |  | 0
EOL

## Lists
Device Type | TIG | TAG | GS6 | GS9 | GS12 | IDPG | Comm Port | Window Contact | Domain | Select TimeZone
IDPG | Btn 1 | Btn 1 | Btn 1 | Btn 1 | Btn 1 | Btn 1 | Ethernet | Show "Open", Never Sleep | RCU1 | UTC-11:00 (American Samoa)
IDPGF | Btn 2 | Btn 2 | Btn 2 | Btn 2 | Btn 2 |  | Wifi on Bus 3 | Show "Open", Go To Sleep | RCU2 | UTC-11:00 (International Date Line West)
IDPGFR | Btn 3 | Btn 3 | Btn 3 | Btn 3 | Btn 3 |  | Wifi on Bus 4 | No Feedback. Tstat Blocked | RCU3 | UTC-11:00 (Midway Island)
TIG |  | Btn 4 | Btn 4 | Btn 4 | Btn 4 |  | Offline | Not Applicable | RCU4 | UTC-10:00 (Hawaii)
TAG1 |  | Btn 5 | Btn 5 | Btn 5 | Btn 5 |  |  |  | RCU5 | UTC-09:00 (Alaska)
TAG2 |  | Btn 6 | Btn 6 | Btn 6 | Btn 6 |  |  |  | RCU6 | UTC-08:00 (Pacific Time (US & Canada))
TAG3 |  | Btn 7 | PIR | Btn 7 | Btn 7 |  | Occupancy Based on |  |  | UTC-08:00 (Tijuana)
TAG4 |  | Btn 8 |  | Btn 8 | Btn 8 |  | Keycard |  |  | UTC-07:00 (Arizona)
TAG5 |  | Btn 9 |  | Btn 9 | Btn 9 |  | Motion Only |  |  | UTC-07:00 (Chihuahua)
TAG6 |  | Btn 10 |  | PIR | Btn 10 |  | Motion & Keycard |  |  | UTC-07:00 (Mazatlan)
GS6 |  | Btn 11 |  |  | Btn 11 |  | Motion with Door Contact |  |  | UTC-07:00 (Mountain Time (US & Canada))
GS9 |  | PIR |  |  | Btn 12 |  | Motion with Door Lock |  |  | UTC-06:00 (Central America)
GS12 |  |  |  |  | PIR |  | Motion with Door Lock and Contact |  |  | UTC-06:00 (Central Time (US & Canada))
IOEXP1 | [6 empty] | Always Occupied |  |  | UTC-06:00 (Guadalajara)
IOEXP2 | [6 empty] | Checkin/Checkout |  |  | UTC-06:00 (Mexico City)
IOEXP3 | [9 empty] | UTC-06:00 (Monterrey)
IOEXP4 | [9 empty] | UTC-06:00 (Saskatchewan)
IOEXP5 | [9 empty] | UTC-05:00 (Bogota)
IOEXP6 | [9 empty] | UTC-05:00 (Eastern Time (US & Canada))
IOEXP7 | [9 empty] | UTC-05:00 (Indiana (East))
IOEXP8 | [9 empty] | UTC-05:00 (Lima)
IOEXP9 | [9 empty] | UTC-05:00 (Quito)
IOEXP10 | [9 empty] | UTC-04:30 (Caracas)
IZT-Bx | [9 empty] | UTC-04:00 (Atlantic Time (Canada))
Nordic | [9 empty] | UTC-04:00 (Georgetown)
cBS Gateway | [9 empty] | UTC-04:00 (La Paz)
UTC-04:00 (Santiago)
UTC-03:30 (Newfoundland)
UTC-03:00 (Brasilia)
Radio | [9 empty] | UTC-03:00 (Buenos Aires)
IZT-Ax | [9 empty] | UTC-03:00 (Greenland)
IZT-Bx | [9 empty] | UTC-02:00 (Mid-Atlantic)
IKT | [9 empty] | UTC-01:00 (Azores)
cBS Gateway | [9 empty] | UTC-01:00 (Cape Verde Is.)
INR03x | [9 empty] | UTC+00:00 (Casablanca)
Nordic | [9 empty] | UTC+00:00 (Dublin)
DC | [9 empty] | UTC+00:00 (Edinburgh)
N/A | [9 empty] | UTC+00:00 (Lisbon)
UTC+00:00 (London)
UTC+00:00 (Monrovia)
UTC+00:00 (UTC)
UTC+01:00 (Amsterdam)
UTC+01:00 (Belgrade)
UTC+01:00 (Berlin)
UTC+01:00 (Bern)
UTC+01:00 (Bratislava)
UTC+01:00 (Brussels)
UTC+01:00 (Budapest)
UTC+01:00 (Copenhagen)
UTC+01:00 (Ljubljana)
UTC+01:00 (Madrid)
UTC+01:00 (Paris)
UTC+01:00 (Prague)
UTC+01:00 (Rome)
UTC+01:00 (Sarajevo)
UTC+01:00 (Skopje)
UTC+01:00 (Stockholm)
UTC+01:00 (Vienna)
UTC+01:00 (Warsaw)
UTC+01:00 (West Central Africa)
UTC+01:00 (Zagreb)
UTC+01:00 (Zurich)
UTC+02:00 (Athens)
UTC+02:00 (Bucharest)
UTC+02:00 (Cairo)
UTC+02:00 (Harare)
UTC+02:00 (Helsinki)
UTC+02:00 (Istanbul)
UTC+02:00 (Jerusalem)
UTC+02:00 (Kyiv)
UTC+02:00 (Pretoria)
UTC+02:00 (Riga)
UTC+02:00 (Sofia)
UTC+02:00 (Tallinn)
UTC+02:00 (Vilnius)
UTC+03:00 (Baghdad)
UTC+03:00 (Kuwait)
UTC+03:00 (Minsk)
UTC+03:00 (Moscow)
UTC+03:00 (Nairobi)
UTC+03:00 (Riyadh)
UTC+03:00 (St. Petersburg)
UTC+03:00 (Volgograd)
UTC+03:30 (Tehran)
UTC+04:00 (Abu Dhabi)
UTC+04:00 (Baku)
UTC+04:00 (Muscat)
UTC+04:00 (Tbilisi)
UTC+04:00 (Yerevan)
UTC+04:30 (Kabul)
UTC+05:00 (Ekaterinburg)
UTC+05:00 (Islamabad)
UTC+05:00 (Karachi)
UTC+05:00 (Tashkent)
UTC+05:30 (Chennai)
UTC+05:30 (Kolkata)
UTC+05:30 (Mumbai)
UTC+05:30 (New Delhi)
UTC+05:30 (Sri Jayawardenepura)
UTC+05:45 (Kathmandu)
UTC+06:00 (Almaty)
UTC+06:00 (Astana)
UTC+06:00 (Dhaka)
UTC+06:00 (Novosibirsk)
UTC+06:00 (Urumqi)
UTC+06:30 (Rangoon)
UTC+07:00 (Bangkok)
UTC+07:00 (Hanoi)
UTC+07:00 (Jakarta)
UTC+07:00 (Krasnoyarsk)
UTC+08:00 (Beijing)
UTC+08:00 (Chongqing)
UTC+08:00 (Hong Kong)
UTC+08:00 (Irkutsk)
UTC+08:00 (Kuala Lumpur)
UTC+08:00 (Perth)
UTC+08:00 (Singapore)
UTC+08:00 (Taipei)
UTC+08:00 (Ulaanbataar)
UTC+09:00 (Osaka)
UTC+09:00 (Sapporo)
UTC+09:00 (Seoul)
UTC+09:00 (Tokyo)
UTC+09:00 (Yakutsk)
UTC+09:30 (Adelaide)
UTC+09:30 (Darwin)
UTC+10:00 (Brisbane)
UTC+10:00 (Canberra)
UTC+10:00 (Guam)
UTC+10:00 (Hobart)
UTC+10:00 (Magadan)
UTC+10:00 (Melbourne)
UTC+10:00 (Port Moresby)
UTC+10:00 (Solomon Is.)
UTC+10:00 (Sydney)
UTC+10:00 (Vladivostok)
UTC+11:00 (New Caledonia)
UTC+12:00 (Auckland)
UTC+12:00 (Fiji)
UTC+12:00 (Kamchatka)
UTC+12:00 (Marshall Is.)
UTC+12:00 (Wellington)
UTC+12:00 (Nuku’alofa)
UTC+12:00 (Samoa)
UTC+13:00 (Tokelau Is.)